## Sheet1
LOT2: Rehabilitation of Three Water Complexes in Karma (Albuabeed & Albukadhem, Karaghool 1, Karaghool 2)
Item # in BOQ | Item | Required Specifications | Submitted Specifications
Items No.1 in Parts 1st, 2nd and 3rd | Horizontal case pump of (200m3/hrx60m) capacity | Capacity: (200m3/hrx60m) Shaft: Stainless steel; Open: 12",with electrical starter; Impeller: bronze; Motor: IP55; Isolation class: f; Electrical engine: 200-250kW; Voltage: 380 – 400 Va; Speed: 1500 RPM; Main frequency: 50hz; Enclosure class: 55; Rated: v3 phase. Certificate of origin and BV inspection are required.
Items No.2 in Parts 1st, 2nd and 3rd | Submersible pump of (210m3/hr*20m) capacity | Capacity: (210m3/hr*20m) Power: 22 kW RPM: 1500 Certificate of origin and BV inspection are required.
Items No.4 in Parts 1st, 2nd and 3rd | Chlorine injection device of 2kg/hr capacity | 2 kgm/h capacity with the injector + booster pump (5m3/hrx100m) + operation board + heater + metal pipe from the bottol to the device with the lock + protection chlorine gas mask + PVC pipes of suitable diameter for chlorine device with the bends, divisions, locks + gas filter
Items No.5 in Parts 1st, 2nd and 3rd | Alum injection pump of (300 litre/h) capacity | 300 litre/hr capacity - shaft and impeller are stainless stee tank + mixer + electrical conections + all PVC pipes, locks and other accessories
Items No.15 in Parts 1st,No 17 in 2nd and No 16 in 3rd | Generator of 250 kVA capacity | General features: - Soundproof and weatherproof canopy - Oil and fuel filter fitted, water separator - Lube-oil drain valve fitted - Electric starter motor 24 V. D.C Ambient temperature : Maximum:55/C Minimum:-10/C Relative Humidity : 92% maximum Altitude: 1000M above MSL System Voltage : 400V No of phase : 3PH Frequency: 50Hz Guarantee: One year ,1000h / operation Generator output Range 250 KVA prime load Maine MCCB breaker 4pole A… Daily base tank Minimum 8 -10 hour fuel capacity Reference standards: IEC/ISO Engine : RPM: Maximum 1500 Prime capacity: 250 KVA prime load Type of Governor: Mechanical /Electronic Overload rating: As per International standard Fuel filter : Standard water separator filter Type of fuel : Diesel Type of starting 24Volt DC Type of cooling: Radiator–fan cooled–fan to be driven by the engine shaft Indicator Turbocharge ALTERNATOR :- Rated Voltage : 0.4 KV Rated power factor : Between 0.8 and 1 No. of Phase : 3Ph Frequency: 50Hz Type of excitation: Brushless, self-regulation Percentage voltage regulation : + 5% IP : Not less than 23 Insulation type : Class H AVR type : Digital CONTROL PANEL :- CONTROLLER INFORMATION Instrumentation Voltmeter and Ammeter Combined frequency and tachometer Hours run counter Voltmeter phase selector switch Ammeter phase selector switch SHUTDOWNS Low Oil Press. High Eng. Temperature
Items No.14 in Parts 1st No,16 in2nd and No 15 in 3rd | Transformer of 250 kVa capacity | Rated Voltage :11-0.416 kV ; Rated KVA :250KVA ; Rated power factor :0.8; No. of Phase: 3Ph ; Highest system voltage:12000 volts; System:3- phase,3-wire with neutral isolated but provision is made for earthling through an earthling resistance of 21.1 ohms to limit, The earth fault current to 300 Amp; Nominal voltage system : 416/240 volts s; Short circuit level: According to the short circuit level of H.T side and the rated power of the transformer; Short circuit level: 25 KA at 11000 volts; Frequency:50Hz ; Interphase Connection: H.V. Delta L.V- star with neutral brought out; Vector relationship : Dyn 11; Type of Cooling: ONAN ; Type :Outdoor type ; Tapings change: five tapping for – 2.5% - 5% on the H.T winding for off Circuit operation externally. The machine must be of the robust and definite position type with a click indicating position arrived during tap changing