Section 10 –
Compliance Sheet 
ITB 116/17 Supply & Install Medical Oxygen Gas Plant in Tikrit Educational Hospital

The following Technical data shall be furnished and filled by the bidders:
1-	Medical Oxygen Plant
UNDP specifications	Bidders’ Offered specifications	
Medical liquid Oxygen plant best quality, with purity not less than 99% by method of Air separation and liquefaction process (Cryogenic System) working by initial pressure (33) bar and Capacity (130) m3/hr		
General features:		
•	Unique Stainless Steel Column with Flange connections and Argon Welding for Accessibility and servicing.		
•	Skid Mounted Technology makes the plant Compact and easy to Install.		
•	Efficient Heat Exchange to attain Minimum Power Consumption and hence minimizing Cost of Operation.		
•	Special Cross-Flow design Stainless Steel Trays for Highest possible Purity.		
•	Special Grade molecular sieves for Total Carbon Dioxide, Moisture and Hydrocarbon Removal.		
•	Trouble Free 24 Hours Continuous Duty operation due To Proven Design and Performance of Stainless Steel plant.		
•	One Operator required running the Plant.		
•	Built in Liquid Oxygen – Oxygen Filling.		
•	Built in Integral Gas Vaporizer to increase the efficiency of the plant.		
•	Medical Grade Oxygen due to Stainless Steel Column as Per American / European Pharmacopoeia.		
•	Extremely Safe to Use and Simple Operate.		
•	Air Compressor (4 Stage). Can be operated both by normal 
    power supply as well DG Set 415V 50 Hz.		
•	An Industrial   refrigerator (chilling plant) having   air cooling facility both before and   after drier battery is included in our scope of supply.		
•	Online portable Oxygen Purity analyzer		
•	 Liquid Pumps are supplied with non-lubricated cross head and therefore are hazard free for Oxygen Pumping. 		
•	A special bypass valve is provided for quick production and better cooling. (R-4)		
•	High quality insulation to prevent cold loss.		
•	High standard of purity of gases.		
•	International class   of   pressure   differential   gauges as fool proof liquid level indicators with Stainless Steel control Panel.		
•	Equipped   with   a very efficient   expansion   engine which helps rapid    and    adequate   cooling.   On account of a very efficient Expansion engine with our plant. The plant operates very stable with consistency   of    purity of    gases.		
•	Low power consumption, as our Plant design is low Pressure cycle		
•	Fool proof temperature indicating system-Electronic scanner		
•	Low maintenance cost.		
•	Safe to operate.		
•	Plants layout, foundation, drawings for easy & economical installation.		
•	Cooling water temperature         300 C (av.)    350 C (Max)		
•	Water filtered 2 stages 		
Technical Characteristics		
Air Compressor Capacity	
:	
734 M3/Hr.at 45 kg/Cm2.	

Starting Pressure	
:	
45 kg/cm2	

Operating Pressure	
:	
30 – 33 kg/cm2	

Starting time till  production	
:	
7 Hrs.	

Defrosting time	
:	
4/6 Hrs.	

Defrosting cycle at normal condition	
:	
12 months	

Power supply required	
:	
420V 220V 3Phase 50 Hz	

Rated through put of liquid Oxygen Pump	
:	
140 M3/Hr.	

Delivery Pressure of pump	
:	
165 kg/cm2.	

Cylinder connections, filling manifold	
:	
2 x 12 Oxygen	

Cooling water requirement 	
:	
40 M3/Hr. (Re-circulated)	

Make-up water requirement	
:	
Approx. 0.5 M3/Hr.
(depending upon cooling tower and ambient condition)	

Insulation 	
:	
Perlite.	

Assembly Height	
:	
8.0 meters.	

Area required	
:	
200 sq.mtrs.	

Material of construction	
:	
Copper, Brass, Steel etc.	

Power consumption	
:	
1.1 units/M3 of Oxygen Gas Produced.	

Motor capacities of Units		
1-	Air Compressor Motor  180 Hp		
2-	Expansion Engine Motor 10 Hp		
3-	Chilling plant motor        3.5 Hp		
4-	Water Pump motor             5 Hp		
5-	Cooling tower motor          5 Hp		
6-	Liquid Oxygen pump motor 7.5 Hp		
7-	Defrosting Heater               9 KW		
8-	Molecular Battery Heater   24 KW		
Submit Manufacturer certification:		
Submit Detail drawing brochure catalogue		

2-	Online Oxygen Purity Analyzer

UNDP specifications		Bidders’ Offered specifications	
3-	High Quality portable online Oxygen Purity Analyzer			
 Measurement ranges:	10~99.99% / 50~99.99% / 80~99%		
Flow rate:	150~300mL/min		
Power supply:
	85~265V. AC, 50/60Hz		
Calibration cycle:	every 360days		
Accuracy:	±0.5%F.S; ±0.1%		
Resolution:	0.01%		
Signal output:
	4-20mA analog output		
Preheat time: 	300s;		
 Response Time	90% in 15 seconds;		
Submit Manufacturer certification:			
Submit Detail drawing brochure catalogue			

4-	Oxygen cylinder test pressure equipment

UNDP specifications		Bidders’ Offered specifications	
High Quality Portable Oxygen Cylinder Test Pressure Equipment
	steel bottle test pressure loading machine is for the test in the resist pressure, the volume distortion and the loading & unloading the bottle valve on the steel bottle (oxygen, hydrogen, nitrogen and CO2 etc.) by “a steel bottle safety monitor procedure”, according to the requirements for the steel bottle inspection and the bottle valve loading & unloading 		
Steel bottle test pressure loading machine is composed of two parts	1. a loading bottle valve device and a returning water device; 2. an electric test pressure pump and a measuring cylinder		
Machine gathers machinery, electricity and pneumatics and can realize the following three functions:	The loading & unloading the bottle valve;
b. The water pressure intensity test, the volume distortion measure & test;
c. The turning over for water fall.
		
Equipment structure is fastness, the performance is reliable, the technology is advanced, the operation is easy, which is a necessary use device in the steel bottle manufacturer, the steel bottle inspection and the filling gas station.			
Performance Parameters	
The rational water test pressure             P1=22.5MPa
2. The valve automatic control wrest moment on the spindle       M1=300N·m
3. The maximal wrest moment on the spindle gas valve           M2=450N·m
4. The returning water angle                     R=145O
5. The drive motor
     The model           Y90S-4
     The power           1.1KW
     The rotation speed           1390r/min
6. The power source:     380V/50HZ
7. The gas source:     P=0.7-0.8Mpa(a safety gas)
8. The top & bottom stroke of the spindle         S1=530mm
9. The stroke of the steel bottle clamping machine     S2=100mm
10. The outer size:(length×width×height)
           a. The main body size:1000×600×3000
b. The electric operation station:600×450×1150
(The electric box without the test pressure pump is installed on the main body of the equipment)
c. The electric test pressure pump: 655×480×1055
11. The weight(the main body):750Kg
12. The specification of the measured steel bottle: The diameter   Φ210—Φ220
   The height     H=1200-1600			
Submit Manufacturer certification:		
Submit Detail drawing brochure catalogue			

5-	Water jet cleaning machine / portable oxygen cylinder

UNDP specifications		Bidders’ Offered specifications	
6-	Water jet cleaning machine / small portable oxygen cylinder	1.	High performance 
2.Unique BIO function design 
3.CE		
Technical Features:			
 1. Non-invasive physical scrub rejuvenation technology
2. No need to configure the dangerous oxygen bottles, it can also achieve the 6-8Kg
pressure
3. Unique design of the sprayer with strong pressure
4. With air compressed fluid recycle and refrigeration plant.
5. Equipped with pulse oxygen spray technique.
6. The latest micro current technology.
7. Fashion design for jet handset with three nozzles.
9. O2 spray technology with product infusion			
Technical Parameters 			
Voltage	AC 110/220 V 50-60 HZ		
Power	< 750 W		
Output Pressure	0~8 Kg		
Micro current Intensity 	1~30		
			
jet spray rate:
	200m/sec
		
Submit Manufacturer certification:		
Submit Detail drawing brochure catalogue		

7-	Diesel Generator 500KVA
UNDP specifications	Bidders’ Offered specifications	
Three phase four wires, output voltages 100-400V, 50HZ, between 0.8 lagging, protection capability abiding by the standards of NEMA1 and IP23.		

General features:
●	Composed of western diesel engine and European Type alternator
●	Oil and fuel filter fitted, water separator
●	Lube-oil drain valve fitted
●	Electric starter motor 24 V. D.C
●	Output range: Prime-500kVA / Standby-550KVA
●	Engine model: 2506(A or C)-E15TAG2
●	Induction system: Turbocharged
●	8-hour operation base tank
●	Key start / auto start
●	Mechanical /Electrical governor
●	4 pole MCCB, set mounted starting battery
●	Soundproof or weatherproof canopy
●	Operation & Maintenance manual
●	Special Integrated Steel Base tank and sprayed overall in gloss enamel paint		
Engine Specifications
In-line direct injection 6-cylinder diesel engine.
Type
Water cooled, four cycle, Turbocharged
Construction
Two valves per cylinder, forged steel crankshaft and
Connecting rods, cast iron block.
Starting 24 volt negative earth. battery charging
Alternator 35 amp on engine. Cranking current 640 amps at 0oc.
Fuel System
24 volt fails safe actuator. Spin-on paper
element fuel filters with Bosch fuel pump injection
system with integral
Electronic governor. Dual flexible fuel lines And connectors. Standard fuel water separator. Filters.
Air cleaner with dry element and restriction indicator.
Spin full flow lube oil filter. Oil cooler. Drain Tap		
Control Panels
Standard Control Function
●	Under / Over Mains Volts /Frequency
●	External Remote control start output (load /
un-load)
●	Configurable relay outputs
●	Synchronization auto / synchronization output
●	All function telecom remote control
●	Engine and Alternator instrumentation monitor
●	Configurable input trip point by 9 users
●	4 user output trip point
●	Control LCD brightness in low brightness environment
●	PIN password
●	Send SMS via GSM modem
●	Reflect load relay output
•Control vary trip point		
●	AC ALTERNATOR
Alternator Technical Data European Type AC alternator
●	Brushless, self-exciting
●	Class ‘H’ insulation
●	Standard degree of protection is IP23
●	Self-regulating
●	With fan cooling
●	Resist humid grease
●	AC excitation, rotating rectification tube
●	Stator grease insulation covered
●	Rotator and excitation high polymer, Resist the corruption of oil and acid.
●	Rotator balance is in accordance with BS5625 standard 12.5
●	High-quality lubrication sealed long-time bearing
●	Rotator silicon steel close tight		
Submit Manufacturer certification:		
Submit Detail drawing brochure catalogue