## 1. SKS & Wi-Fi
POZICIJA/ITEM | OPIS/ DESCRIPTION | JEDINICE/ UNITS | KOLIČINA/ QUANTITY | x | JEDINIČNA CIJENA/ UNIT PRICE | UKUPNA CIJENA/ TOTAL PRICE
PREDMJER I PREDRAČUN / PRICED BILL OF QUANTITIES
SKS i Wi-Fi INSTALACIJE U OBJEKTU/ SKS and Wi-Fi INSTALLATIONS IN THE FACILITY
1 | Izrada kablovske kanalizacije sa 4PE ili PEHD cijevi presjeka 50mm, od pozicije ormara koncetracije -rek ormara planiranog objekta do pozicije najbližeg kablovskog okna postojeće kablovske kanalizacije. Stavka uključuje kom/pcsplet materijal i radove, isporuku i polaganje cijevi, iskop i zatrpavanje rova dimenzija (70x25)cm. /Construction of cable ducts with 4PE or PEHD 50mm section pipes, from the location of the concentration cabinet – rack cabinet of the planned facility to the location of the nearest cable box of the existing cable ducts. The item includes all materials and works, delivery and laying of pipes, digging and backfilling of a trench measuring (70x25) cm. | m | 70 | x |  | 0
2 | Izrada priključnog kablovskog okna unutrašnjih dimenzija (100x100x100)cm. Stavka uključuje kom/pcsplet materijal i zemljane i građevinske radove i isporuku i montažu lakog rama sa poklopcem./ Making the connection cable box measuring (100x100x100) cm inside. The item includes all materials, earthwork and construction work, and supply and a light frame installation with a cover. | kom/pcs | 1 | x |  | 0
3 | Isporuka i provlačenje singlomodnog optičkog kabla sa 24 optička vlakna od pozicije planiranog rek ormara u novom objektu do pozicije centra nadzora u postojećem objektu./Supply and delivery of a single mode optical optic cable with 24 optical fibers from the location of the planned rack cabinet in the new facility to the location of the monitoring center in the existing facility. | m | 250 | x |  | 0
4 | Slobodnostojeći 19" rack orman, visine 47HU, dimenzija 800x1000mm (ŠxD), sa staklenim vratima i ključem, opremljen sa ventilator panelom koji se montira na krov i sadrži četiri ventilatora sa filterima za prašinu i termostatom za kontrolu rada ventilatora , sličan tipu SCHRACK DS228010-A,. sa kom/pcspletnom pratećom montažnom opremom.Ukupno za isporuku i montažu./The freestanding 19 "rack cabinet, height 47HU, measuring 800x1000mm (WxD), with glass door and key, equipped with a roof mounted fan ventilator panel that contains four fans with dust filters and fan control thermostats similar to the SCHRACK DS228010- A, with full associated mounting equipment. Total delivery and installation. | kom/pcs | 2 | x |  | 0
5 | Patch panel 19'', 1 HU, modularnog tipa, prazan, za smeštanje 24xRJ45 modula, sličan tipu SCHRACK HSER0240GS;/Patch panel 19 '', 1 HU, modular type, empty, for mounting a 24xRJ45 module, similar to SCHRACK HSER0240GS; | kom/pcs | 10 | x |  | 0
6 | Isporuka i montaža 19'', 24-portnog optičkog patch panela , 2 HU, modularnog tipa. /Delivery and installation of 19 ", 24-port optical patch panel, 2 HU, modular type. | kom/pcs | 2 | x |  | 0
7 | Modul Cat.6a 10GB STP, TOOLLESS, sastavljanje bez alata, za ugradnju u patch panel ili utičnicu u polju, obeležavanje, sličan tipu SCHRACK HSEMRJ6GWT;/Cat.6a Module 10GB STP, TOOLLESS, assembly without tools, for patch panel mounting or field socket, marking, similar to SCHRACK HSEMRJ6GWT; | kom/pcs | 240 | x |  | 0
8 | Nosač kablova za horizontalno vodjenje kablova, patch guide, sa kanalicom, 19", 1HU, slično tipu SCHRACK HDBS148051;/Cable carrier for horizontal cable management, patch guide, with channel, 19 ", 1HU, similar to SCHRACK HDBS148051; | kom/pcs | 12 | x |  | 0
9 | Fiksna polica 19", 350mm, za rack orman dubine 395mm, 1HU, nosivosti 15 kg, slična tipu SCHRACK DFS14835-C;/Fixed shelf 19 ", 350mm, for a rack cabinet, 395mm deep, 1HU, 15 kg capacity, similar to SCHRACK DFS14835-C; | kom/pcs | 6 | x |  | 0
10 | Napojna šina sa 7 utičnica i prekidačem, 230Vac 50Hz,slična tipu SCHRACK IU070107-B/Power cable with 7 sockets and switch, 230Vac 50Hz, similar to SCHRACK IU070107-B | kom/pcs | 1 | x |  | 0
11 | Isporuka i montaža F/FTP instalacionog kabla, Cat.6a, 4x2xAWG23, 500MHz, sa omotačem bez halogenih elemenata (LS0H), PIMF, sličan tipu SCHRACK HSEKP423HC, dijelom kroz kablovski regal a dijelom kroz PVC Ø13 cijevi, zidovima i po podu od RACK-a na prizemlju objekta do SKS prikljucnica, Wi-fi AP, pozicija kamera i monitora u objektu. Kablove spojiti na PATCH panel u RACK-u, prema grafičkim prilozima u prilogu ovog projekta. Prosječna dužina provodnika po instalaciji iznosi 40m. U obračun su uračunati radovi, kabal i cijevi po dužnom metru.Stavka uključuje i kablove za Wi-Fi internet, kablove sistema video nadzora i kablove za monitore./Delivery and installation of a F/FTP installation cable, Cat.6a, 4x2xAWG23, 500MHz, with non-halogenic coat (LS0H), PIMF, similar to SCHRACK HSEKP423HC, partly through cable reel and partly through PVC Ø13 tubes, walls and floor of RACK on the ground floor of the building to the SKS terminal, Wi-fi AP, camera and monitor position in the building. Connecting the cables to the PATCH panel in the RACK, according to the graphic attachments attached to this design. The average cable length per installation is 40m. The calculations include works, cables and pipes measured per meter. The item also includes wires for Wi-Fi internet, video surveillance systems cables, and monitor cables. | kom/pcs | 257 | x |  | 0
12 | Telekomunikaciona utičnica, modularna, ravna, za 2xRJ45 konektora, za ugradnju u zid, tipa Bticino ili slična . Uskladiti sa energetskim programom. Ukupno za isporuku i montažu:/Telecommunication socket, modular, flat, for 2xRJ45 connectors, for wall mounting, type Bticino or similar. Match with the energy program. Total for delivery and assembly: | kom/pcs | 2 | x |  | 0
13 | Telekomunikaciona utičnica, modularna, ravna, za 3xRJ45 konektora, za ugradnju u zid, tipa Bticino ili slična . Uskladiti sa energetskim programom. Ukupno za isporuku i montažu:/Telecommunication Socket, modular, flat, for 3xRJ45 connectors, for wall mounting, type Bticino or similar. Match with the energy program. Total for delivery and assembly: | kom/pcs | 17 | x |  | 0
14 | Telekomunikaciona utičnica, modularna, ravna, za 4xRJ45 konektora, za ugradnju u zid ili pod, tipa Bticino ili slična . Uskladiti sa energetskim programom. Ukupno za isporuku i montažu:/Telecommunication Socket, modular, flat, for 3xRJ45 connectors, for wall mounting, type Bticino or similar. Match with the energy program. Total for delivery and assembly: | kom/pcs | 14 | x |  | 0
15 | Telekom komunikaciona utičnica, modularna, ravna, za 6xRJ45 konektora, za ugradnju u zid ili pod, tipa Bticino ili slična . Uskladiti sa energetskim programom. Ukupno za isporuku i montažu:/Telecommunication socket, modular, flat, for 6xRJ45 connectors, for wall or floor mounting, type Bticino or similar. Match with the energy program. Total for delivery and assembly: | kom/pcs | 5 | x |  | 0
16 | Telekomunikaciona utičnica, modularna, kosa, za 1xRJ45 konektora, slična tipu za ugradnju na zid u spuštenom plafonu za potrebe video nadzora i wirelessa TOOLLESS LINE, pozicija monitora slična tipu Schrack ukupno za isporuku i montažu/Telecommunication socket, modular, inclined, for 1xRJ45 connectors, similar to wall mount for suspended ceilings for video surveillance and wirelessa TOOLLESS LINE, monitor position similar to Schrack type total for delivery and installation | kom/pcs | 82 | x |  | 0
17 | Kratkospojni FTP patch cable RJ45, dužine 1m za priključivanje kamera,monitora, WI-Fii uređaja i priključivanje opreme u rekovima. Nabavka, isporuka, montaža i povezivanje/FTP patch cable RJ45, 1m long for connecting cameras, monitors, WI-Fi devices, and connecting equipment to recks. Purchase, delivery, mounting and connection | kom/pcs | 257 | x |  | 0
18 | Završna mjerenja na F/ FTP kablovima sa izradom mjernog protokola i izdavanjem atesta/Final measurement on F / FTP cables with measurement protocol design and issuance of certificate of test | kom/pcs | 257 | x |  | 0
19 | 48-portni switch J9775A Aruba 2530 48G, za SKS mrežu /48-port switch J9775A Aruba 2530 48G, for SKS network | kom/pcs | 3 | x |  | 0
20 | SFP Modul 10GB/SFP Module 10GB | kom/pcs | 3 | x |  | 0
SEGMENT VI- WI FI internet
21 | Ruckus ZONEFLEX R610 Unutrašnja 802.11ac/n MU-MIMO Wave 2 3x3:3 Wi-Fi pristupna tačka Hardver mora biti registrovan za projekat Aerodrom Tivat od strane proizvođača Jednovremeni protok 1.3Gbps (5GHz) i 600Mbps (2.4GHz) BeamFlex+ za do 4dB SINR pojačanje signala i do 10 dB ublažavanja interferencije. PD-MRC, ChannelFly, Smart meshing Podržava do 512 klijenata po pristupnoj tački Sposobnost da podrži 80+80/160 MHz kanale USB port podržava BLE/IoT, 2 Ethernet porta (1 PoE) /"Ruckus ZONEFLEX R610 Internal 802.11ac/n MU-MIMO Wave 2 3x3: 3 Wi-Fi Access Point Hardware must be registered for the Tivat Airport Project by the manufacturer Single Stream 1.3Gbps (5GHz) and 600Mbps (2.4GHz) BeamFlex + for up to 4dB SINR signal amplification and up to 10 dB for interference suppression. PD-MRC, ChannelFly, Smart meshing Supports up to 512 clients per access point Ability to support 80 + 80/160 MHz channels USB port supports BLE / IoT, 2 Ethernet ports (1 PoE) " | kom/pcs | 8 | x |  | 0
Dualno polarizovane adaptivne antene sa do 1024 šeme Router mod sa NAT i DHCP servisima, IP multicast podrška WPA-PSK (AES), 802.1X podrška za RADIUS i Active Directory, dinamičku PSK, kontrolu povezivanja/balansiranje opterećenja, prebacivanje opsega i airtime fairness Captive portal i gostinski nalozi Prepoznavanje i kontrola aplikacija, SmartWay Bonjour gateway, Hotspot 2.0, SPOT lokacijski servisi Isporuka, montaža./Dual polarized adaptive antennas with up to 1024 router Modem routers with NAT and DHCP services, IP multicast support WPA-PSK (AES), 802.1X support for RADIUS and Active Directory, dynamic PSK, load balancing / balancing control, bandwidth and airtime fairness Captive portal and guest orders Application recognition and control, SmartWay Bonjour gateway, Hotspot 2.0, SPOT location services Delivery, installation./Dual polarized adaptive antennas with up to 1024 router Modem routers with NAT and DHCP services, IP multicast support WPA-PSK (AES), 802.1X support for RADIUS and Active Directory, dynamic PSK, load balancing / balancing control, bandwidth and airtime fairness Captive portal and guest orders Application recognition and control, SmartWay Bonjour gateway, Hotspot 2.0, SPOT location service Provisioning, installation / Dual polarized adaptive antennas with up to 1024 routers Modem routers with NAT and DHCP services, IP multicast support WPA-PSK (AES) , 802.1X support for RADIUS and Active Directory, Dynamic PSK, Load Balancing / Balance Control, Bandwidth and Airtime Fairness Captive portal and guest orders Application recognition and control, SmartWay Bonjour gateway, Hotspot 2.0, SPOT location services Delivery, installation.
22 | Ruckus ZONEFLEX R710 802.11ac/n Wave 2 Wi-Fi pristupna tačka MU-MIMO 4x4:4 spremna za IoT Hardver mora biti registrovan za projekat Aerodrom Tivat od strane proizvođača BeamFlex+ dualno polarizovane adaptivne antene za do 5dB SINR pojačanje signala i do 15dB ublažavanja interferencije. Jednovremeni protok 1733Mbps (5GHz) i 800Mbps (2.4GHz), 80 MHz kanali; 256-QAM podrška; PD-MRC, ChannelFly, Smart meshing, 2 Ethernet porta sa agregacijom linkova (LACP)/"Ruckus ZONEFLEX R710 802.11ac / n Wave 2 Wi-Fi access point MU-MIMO 4x4: 4 ready for IoT Hardware must be registered for the Tivat Aerodrome Project by the manufacturer BeamFlex + dual polarized adaptive antennas for up to 5dB SINR signal amplification and up to 15dB mitigating interference. Single Stream 1733Mbps (5GHz) and 800Mbps (2.4GHz), 80MHz channels; 256-QAM support; PD-MRC, ChannelFly, Smart meshing, 2 Ethernet link aggregation ports (LACP) | kom/pcs | 1 | x |  | 0
Istovremena podrška za multicast HD IPTV, VoIP i data Podržava do 512 klijenata USB port za hosting IoT uređaja (BLE pametni bikoni) Spot triangulacija, SmartFlex lociranje i analitika Do 16 BSSID po radju sa jedinstvenim QoS i politikama bezbednosti Integrisana NAT i DHCP podrška WPA-PSK (AES), podrška za 802.1X za RADIUS i AD, Zero-IT i dinamičku PSK, kontrolu povezivanja/balansiranje opterećenja, prebacivanje opsega Captive portal i gostinski nalozi Isporuka, montaža./ "Simultaneous support for multicast HD IPTV, VoIP and data Supports up to 512 clients USB port for hosting IoT devices (BLE smart beacons) Spot triangulation, SmartFlex locating and analytics Up to 16 BSSIDs per radio with unique QoS and security policies Integrated NAT and DHCP WPA-PSK (AES) support, 802.1X support for RADIUS and AD, Zero-IT and Dynamic PSK, Load Link / Balance Control, Captive Portal and guest orders Delivery, assembly. "
23 | Ruckus Zone director 1205 or SZ 100 Pametni Wi-Fi kontroler za pristupne tačke Hardver mora biti registrovan za projekat Aerodrom Tivat od strane proizvođača Sa 3+1 aktivnim grupisanjem, podržava do 3 000 AP i 60 000 klijenata sa punom redundansom. Mrežna statistika sa skladištenjem podataka do 30 dana o AP i klijentima./"Ruckus Zone director 1205 or SZ 100 Smart Wi-Fi Access Point Controller Hardware must be registered for the Tivat Airport Project by the manufacturer with 3 + 1 active grouping, supports up to 3,000 APs and 60,000 clients with full redundance. Network statistics with storing data on AP and clients up to 30 days." | kom/pcs | 1 | x |  | 0
10 Gbps protok podataka po čvoru Licence se slobodno i lako migriraju u druge SmartZone sisteme Licence se mogu deliti kroz grupu Podrška za autentifikaciju po 802.X, MAC adresi Upravljanje skim mrežnim opcijama/captive portal, DHCP server, SNMP v3, dinamički VLAN-ovi Isporuka, montaža./ "10 Gbps data flow per node Licenses are free and easy to migrate to other SmartZone systems Licenses can be grouped 802X authentication support, MAC address Fixed Network Options / captive portal, DHCP server, SNMP v3, dynamic VLANs Delivery, assembly. "
24 | Ruckus ZD/SZ licence za pristupne tačke Licence se slobodno i lako migriraju kroz sve SmartZone sistem/Ruckus ZD / SZ Access Point License Licenses are free and easy to migrate through all SmartZone systems | kom/pcs | 8 | x |  | 0
25 | Ruckus 7150 48'p PoE floor switch za WiFi, FIDS i rezerva/Ruckus 7150 48'p PoE floor switch for WiFi, FIDS and backup | kom/pcs | 1 | x |  | 0
| SFP Modul 10GB | kom/pcs | 2 | x |  | 0
26 | Patch kabal (0.5 - 1)m/Patch cable (0.5 - 1) m | kom/pcs | 16 | x |  | 0
27 | Montaža opreme u polju/Mounting equipment in the field | kom/pcs | 8 | x |  | 0
28 | Montaza sistema, konfiguracija i pustanje u rad /Assembly of system, configuration and setting into operation | paus/ lump sum | 1 | x |  | 0
29 | Izrada projekta održavanja/ Maintenance plan preparation | pauš./ lump sum | 1 | x |  | 0
| Ukupno SKS i Wi-Fi instalacije bez PDV-a/Total SKS and Wi-Fi installations without VAT |  |  |  |  | 0
PDV 21%/ VAT 21%
| Ukupno SKS i Wi-Fi sa PDV-om/ Total SKS and Wi-Fi with VAT |  |  |  |  | 0

## 2. Pozar_Fire- Sinteso
SISTEM ZA AUTOMATSKU DOJAVU POŽARA/ FIRE ALARM SYSTEM
Projekat/Project: |  | Aerodrom Tivat - Novi terminal/Tivat Airport - New Terminal
Br. /No. | Oznaka/Code | Naziv/ Title |  | Kol./Quantity |  | Jed.cena/Unit Price | Ukupna cena/ Total Price
1 | FC2030-AA | FC2030-AA Modularna PP centrala sa 2 integrisane Fdnet petlje i još 2 mesta u card cage za proširenje sa karticama za starie tehnologije za povezivanje postojecih Synova detektora, komunikacija sa centralnim sistemom za nadzor i upravljanje preko BacNET protokola/ FC2030-AA Modular PP Center with 2 Integrated Fdnet loops and 2 more locations in card cage to extend existing technology cards to connect the existing Synov detectors, communicate with the central control and management system via the BacNET protocol | kom./pcs | 1 | x |  | 0
|  | Mikroprocesorski kontrolisana adresabilna centrala sistema detekcije požara, zasnovana na komunikaciji sa standardnim i inteligentnim javljačima požara i drugim elementima preko veceg broja petlji kapaciteta max 1500 adresa. Centrala poseduje osvetljeni LCD displej sa 8x40 karaktera za prikaz tekstualnih informacija u mirnom stanju i instrukcija operatoru u alarmnom stanju uz korišćenje odgovarajućeg menija za komunikaciju. /Microprocessor-controlled addressable fire detection system, based on communication with standard and intelligent firewalls and other elements over a larger number of loops with a capacity of up to 1500 addresses. The center has an illuminated LCD display with 8x40 characters to display silent text information and operator instructions in alarm mode using the appropriate communication menus. |  |  |  |  | 0
|  | Opciono, centrala poseduje mogućnost mrežnog povezivanja sa drugim centralama i PP terminalima. Predvidjen je potreban broj programibilnih relejnih izlaza za upravljanje tehničkim sistemima u slučaju požara, kao i mogućnost integracije u sisteme za centralni nadzor I upravljanje. Ugradjena je napojna jedinica (24V/150W) za mrežno napajanje i automatsko punjenje akumulatorske baterije za rezervno napajanje u trajanju od 72 sata u mirnom stanju i dodatnih 30 min. u stanju alarma. Centrala je ugradjena u standardno kućište i osim osnovne opreme, sadrži i sledeće elemente:/Optionally, the center has the possibility of networking with other switches and PP terminals. There is a need for a number of programmable relay outputs for managing technical systems in the event of fire, as well as the possibility of integration into central control and management systems. Built-in power supply (24V / 150W) for power supply and automatic recharging of battery backup battery for 72 hours in silent mode and additional 30 min. in alarm state. The central unit is built into a standard enclosure, and besides the basic equipment, it also contains the following elements: |  |  |  |  | 0
| FCL2005-A1 | FCL2005-A1 Line card (AnalogPLUS) 4 loops per line card (with max. 512 addresses per line card) | kom./pcs | 1 | x |  | 0
0
| FCA2013-A1 | FCA2013-A1 Licencni ključ(L2) za poveivanje sa sistemima za centralni nadzor i upravljanje (MM8000, Desigo...) uključuje i SintesoView/ FCA2013-A1 License key (L2) for connection to central monitoring and management systems (MM8000, Desigo ...) includes SintesoViewFCA2013-A1 License key (L2) for connection to central monitoring and management systems (MM8000, Desigo ...) includes SintesoView | kom./pcs | 1 |  |  | 0
| ParaVox | Automatski telefonski dojavnik/ Automatic phone alarm | kom./pcs | 1 |  |  | 0
| Baterije | Akubaterije 12V27Ah/ Batteries 12V27Ah | kom./pcs | 2 | x |  | 0
0
2. | FDO221 | FDO221 SINTESO C-LINE, Adresabilni automatski optički detektor požara, kompatibilan sa postojecim sstemom/ FDO221 SINTESO C-LINE, Addressable Automatic Optical Fire Detector, Compatible with an Existing System | kom./pcs | 75 | x |  | 0
0
|  | Dimni detektor požara širokog spektra sa analizom požarnih parametara preko detektorskih algoritama (DA) i automatskom kompenzacijom štetnih uticaja. Detektor je otporan na standardne smetnje koje se mogu javiti (prašina, vlakna, insekti, vlažnost, kondenzacija, EM uticaji, korozivne pare, vibracije, udari i sl.). Detektor poseduje opto-elektronsku komoru i optički senzora za detekciju tamnih i svetlih dimnih čestica sa povećanim imunitetom prema lažnim alarmima. Detektor poseduje alarmni indikator vidljiv u u krugu od 360º kao i ugradjeni izolator linije od kratkog spoja i prekida. Detektor se adresira i podešava sa centralnog uređaja, i svi detektori koriste isti tip podnožja. Radna temperatura detektora je -10... +60 °C. Kategorija zaštite je IP43 (IP44 sa dodacima). Detektor je u skladu sa EN54-7, EN54-17 standardima. Detektor poseduje VdS G204018 i LPCB 126ab/02 sertifikate./ "Large-scale fire smoke detector with fire detection analysis via detection algorithms (DA) and automatic compensation of harmful impacts. The detector is resistant to standard interference that may occur (dust, fibers, insects, humidity, condensation, EM influences, corrosive vapors, vibrations, shocks, etc.). The detector has an opto-electronic chamber and an optical detector for detecting dark and light smoke particles with increased immunity against fake alarms. The detector has an alarm indicator visible in a 360º circuit as well as a built-in line isolator for short circuit and interruption. The detector is addressed and adjusted from the central unit, and all detectors use the same type of base. The operating temperature of the detector is -10 ... +60 ° C. The protection category is IP43 (IP44 with add-ons). The detector complies with EN54-7, EN54-17 standards. The detector has VdS G204018 and LPCB 126ab / 02 certificates. " |  |  |  |  | 0
| FDB221 | FDB221 SINTESO, S-LINE, C-LINE Podnožje adresabilnih detektora požara, sa odstojnicima za uvid kabla sa strane maksimalnog prečnika kabla 6mm/FDB221 SINTESO, S-LINE, C-LINE Addressable fire detector base, with cable extension strips on the side of the maximum cable diameter 6mm | kom./pcs | 75 | x |  | 0
|  | Podnožje je izradjeno od sintetičkog materijala otpornog na udarce, vibracije i ogrebotine sa terminalnim kontaktima bez zavrtanja. Prečnik kablova je od 0.2 to 1.5 mm2. Boja podnožja je čisto bela, RAL 9010/ The base is made of synthetic material resistant to impact, vibration and scratches with terminal contacts without screws. The diameter of the cable is 0.2 to 1.5 mm2. Base color is pure white, RAL 9010 |  |  |  |  | 0
| FDB291 | FDB291 Dodatno podnožje za nadgradnju/FDB291 Additional footboard for upgrade | kom./pcs | 75 | x |  | 0
|  | Za uvod kablova prečnika većeg od 6mm; Sa oprugom za povezivanje sa podnožjem; Ukupna visina sa detektorom 60mm. Boja je čisto bela, RAL 9010/ For introduction of diameters of more than 6mm; With spring to connect with the foot; Total height with 60mm detector. The color is purely white, RAL 9010 |  |  |  |  | 0
0
2 | FDAI91 | FDAI91 SINTESO Paralelni indikator požara/FDAI91 SINTESO Parallel fire indicator | kom./pcs | 30 | x |  | 0
|  | Moderni ravan dizajn, povezivanje sa terminalima bez šrafova; Montira se na zid ili plafon, dimenzije 62 x 37 x 24 mm/Modern straight design, connection to terminals without screws; It is mounted on a wall or ceiling, dimensions 62 x 37 x 24 mm |  |  |  |  | 0
0
3. | FDME221 | FDME221 SINTESO Adresabilni ručni javljač požara sa direktnom aktivacijom, kompatibilan sa postojecom centralom Sinteso FC2020/ FDME221 SINTESO Addressable manual fire detector with direct activation, compatible with the existing Sinteso FC2020 | kom./pcs | 12 | x |  | 0
|  | Elektronika ručnog javljača požara sa direktnim aktiviranjem lomljenjem zaštitnog stakla. U javljač je ugradjen izolator linije od kratkog spoja i prekida. Radna temperatura detektora je -25... +70 °C. Kategorija zaštite je IP44. Javljač je u skladu sa EN54-11, EN54-17 standardima. Javljač poseduje VdS G203059 i LPCB 126ap/07 sertifikate/ "Manual fire detector electronics with direct activation by breaking the protective glass. A short circuit breaker and interruption line insulator is installed in the monitor. The operating temperature of the detector is -25 ... +70 ° C. The protection category is IP44. The tracker is compliant with EN54-11, EN54-17 standards. The tracker possesses VdS G203059 and LPCB 126ap / 07 certificates " |  |  |  |  | 0
| FDMH291-R | FDMH291-R Kućište javljača, crveno/ Tracker housing, red | kom./pcs | 12 | x |  | 0
| FDMC291 | FDMC291 Zaštitni poklopac/ protective lid | kom./pcs | 12 | x |  | 0
0
4. | FDS229-R | FDS229-R SINTESO Adresabilna alarmna sirena sa bljeskalicom u crvenoj boji/ FDS229-R SINTESO Addressable alarm siren with flash in red | kom./pcs | 7 | x |  | 0
|  | Alarmna sirena sa bljeskalicom i izborom jednog od 11 tonova u dva nivoa, prema programu. Nivo zvuka do 99 dBA, podesiv u 3 nivoa, sa podesivim načinom rada bljeskalice, posebnim pobudjivanjem sirene i bljeskalice u slučaju alarma i napajanjem i komunikacijom preko zajedničke petlje, uz mogućnost nadzora nad statusom uredjaja. U uredjaj je ugradjen izolator linije od kratkog spoja i prekida. Radna temperatura sirene je -25... +60 °C. Kategorija zaštite je IP43/IP44/IP54 sa dodatkom. Sirena je u skladu sa EN54-3, EN54-17 standardima. Sirena poseduje VdS G207156 sertifikat./ "Alarm siren with flash and choice of one of the 11 tones in two levels, according to the program. Sound level up to 99 dBA, adjustable in 3 levels, with adjustable flash mode, special siren and flash alarm in case of alarm and power and communication over a common loop , with the ability to monitor the status of the device. The unit has a line insulator for short circuit and interruption. The operating temperature of the siren is -25 ... +60 ° C. The protection category is IP43 / IP44 / IP54 with the attachment. The siren is in accordance with EN54-3, EN54-17 standards. Siren possesses VdS G207156 certificate. " |  |  |  |  | 0
0
| FDB221 | FDB221 SINTESO, S-LINE, C-LINE Podnožje adresabilnih detektora požara, sa odstojnicima za uvid kabla sa strane maksimalnog prečnika kabla 6mm/ FDB221 SINTESO, S-LINE, C-LINE Addressable fire detector base, with cable extension strips on the side of the maximum cable diameter 6mm | kom./pcs | 7 | x |  | 0
|  | Podnožje je izradjeno od sintetičkog materijala otpornog na udarce, vibracije i ogrebotine sa terminalnim kontaktima bez zavrtanja. Prečnik kablova je od 0.2 to 1.5 mm2. Boja podnožja je čisto bela, RAL 9010 / The base is made of synthetic material resistant to impact, vibration and scratches with terminal contacts without screws. The diameter of the cable is 0.2 to 1.5 mm2. Base color is pure white, RAL 9010 |  |  |  |  | 0
| FDB291 | FDB291 Dodatno podnožje za nadgradnju, za unutrasnju montazu/FDB291 Additional base for upgrading, for interior mounting | kom./pcs | 3 | x |  | 0
| FDB293 | FDB293 Dodatno podnožje za spoljnu montrazu/ FDB293 Additional foot for outdoor assembly | kom./pcs | 4 | x |  | 0
0
5. | FDCIO222 | FDCIO222 SINTESO Adresabilni ulazno / izlazni modul sa 4 nadzirana ulazoma i 4 relejna izlaza/ FDCIO222 SINTESO Addressable Input / Output Module with 4 Controlled Inputs and 4 Relay Outputs | kom./pcs | 10 | x |  | 0
|  | Mikroprocesorski kontrolisan ulazno / izlazni modul koji poseduje 4 nadzirana kontaktna ulaza, sa LED-om za prikaz statusa, kao i 4 nadzirana relejna izlaza 250 VAC/ 30VDC / 2A. Ulazi su nadzirani na prekid i kratak spoj. Modul se napaja i adresira sa centralnog uređaja preko petlje sa samo dve žice. Modul u sebi poseduje ugradjeni izolator linije od kratkog spoja i prekida. Radna temperatura modula je -25... +60 °C. Kategorija zaštite je IP30 (IP65 sa kućištem FDCH292). Modul je u skladu sa EN54-17, EN54-18 standardima. Modul poseduje VdS G204029 i LPCB 126ad/02/ "Microprocessor controlled input / output module with 4 monitored contact inputs, status display LED, and 4 monitored relay outputs 250 VAC / 30VDC / 2A. Inputs are monitored for interruption and short circuit. The module is powered and addressed from the central unit over a loop with only two wires. The module itself has a built-in line insulator for short circuit and interruption. The operating temperature of the module is -25 ... +60 ° C. The protection category is IP30 (IP65 with FDCH292 enclosure). The module complies with EN54-17, EN54-18 standards. The module has VdS G204029 and LPCB 126ad / 02 " |  |  |  |  | 0
| FDCH221 | FDCH221 Kućište/ FDCH221 Housing | kom./pcs | 10 | x |  | 0
|  | Kućište sa poklopcem i dihtungom za montažu ulazno / izlaznih modula u vlažnoj sredini. Kategorija zaštite IP65. Dimenzije su 207 x 119 x 48 mm. Ne uključuje uvodnice./ Housing with cover and dihtung for installation of input / output modules in the damp environment. Protection category IP65. The dimensions are 207 x 119 x 48 mm. It does not include bunches. |  |  |  |  | 0
0
6 | FT2011-A1 | FT2011-A1 SINTESO Signalni spratni terminal/ FT2011-A1 SINTESO Signal multi-storey terminal | kom./pcs | 1 | x |  | 0
|  | Terminal je opremljen sa osvetljenim LCD displejom (6x40 karaktera), alarmnom porukom, tipkom za isključenje zvučnog signala i tipkama za prelistavnje alarmnih i drugih poruka; Komunikacija sa centralnim uređajem je preko FDnet protokola; Terminal je opremljen i izolatorom linije od kratkog spoja i prekida linije./ The terminal is equipped with an illuminated LCD display (6x40 characters), an alarm message, an audio signal disable key, and scroll keys for other alarms and other messages; Communication with the central device is via the FDnet protocol; The terminal is also equipped with a line short circuit isolator and line breaks. |  |  |  |  | 0
0
| FE180/E30 | Isporuka i polaganje instalacionog negorivog kabla, tipa FE180/E30 JH(St)H 2x2x0.8mm/ Delivery and installation of installation non-conductive cable type FE180 / E30 JH (St) H 2x2x0.8mm | m. | 1050 | x |  | 0
0
|  | Isporuka i polaganje rebrastog creva precnika fi 16mm, bezhalogeno/Delivery and laying of currugated tube 16mm in diameter, nonhalogen | m. | 1050 | x |  | 0
0
| PNK | Isporuka i ugradnja negorivog perforiranog nosaca kablova, OBO Betterman ili slicno/Delivery and installation of non-flammable perforated cable carrier, OBO Betterman or similar | m. | 200 | x |  | 0
0
|  | Montaza opreme u polju: detektora, sirena, rucnih javljaca, ulaznih i izvrsnih modula…/Mounting of equipment in field: detectors, sirens, handwheels, input and executive modules ... | kom./pcs | 134 | x |  | 0
0
|  | Programiranje centranog uredjaja, dodavanje novih elemenata, unosenje korisnickih tekstova, programiranje komandi, primopredaja dokumentacije, obuka korisnika/ Programming Center Devices, Adding New Items, Entering User Texts, Programming Commands, Document Delivery, User Training | paus./ lump sum | 1 | x |  | 0
UKUPNO DOJAVA POZARA - NOVA TERMINALNA ZGRADA/TOTAL FIRE ALARM - NEW TERMINAL BUILDING | [6 empty] | 0
PDV/VAT |  |  |  | 0.21 |  |  | 0
UKUPNO DOJAVA POZARA SA PDV-om/TOTAL FIRE ALARM WITH VAT | [6 empty] | 0

## 3. Dojava provale_Burglar alarm
SISTEM ZA DETEKCIJU PROVALE/BURGLAR ALARM SYSTEM
Projekat/Project: |  | Aerodrom Tivat - Novi terminal/ Airport Tivat - New Terminal
Br. /No. | Oznaka/Code | Naziv/ Title |  | Kol./Quantity |  | Jed.cena/Unit Price | Ukupna cena/ Total Price
1. | AGB600 | AGB600, Ambijentalni detektor loma stakla/Ambient glass break detector | kom./pcs | 20 | x | 0 | 0
|  | Mikroprocesorska analiza signala; Pogodan za primenu na velikim i malin staklenim površinama, za jednostruka ili višesturka stakla; Pogodna i za armirana stakla i laminirane slojeve; Automatsko samotestiranje i podešavanja; Mala potrošnja od 3,2 (8) mA; Radijus detekcije od maksimum 8,5 m; Bele boje i atraktivnog dizajna; Radna temperatura -10 ~ +55°C; VdS atest/Microprocessor signal analysis; Suitable for use on large and small glass surfaces for single or multiple glass; Also suitable for reinforced glass and laminated layers; Automatic self-testing and adjustments; Low consumption of 3.2 (8) mA; Detection radius of maximum 8.5 m; Colorful colors and attractive design; Operating temperature -10 ~ + 55 ° C; VdS certificate of test |  |  |  | 0
0
2 | IR120MD | Swisstec PIR detektor, 12m širokougaoni/Swisstec PIR detector, 12m wideband | kom./pcs | 19 | x | 0 | 0
|  | Digitalni infracrveni Swisstec detektor sa obradom signala preko AMASIC posvećenog čipa, tripleks optika sa crnim ogledalom i otpornošću na male životinje do 40 kg; Stvarna kompenzacija promena temperature; Ugrađen filter belog svetla; Potpuno zašitćen od prodora insekata i elektromagnetnih uticaja; Oblast detekcije 12m x 12m; Četiri nivoa osetljivosti; Radna temperatura -20°C do +50°C, IP41 kategorija zaštite; Ultra mala potrošnja od 6mA/ Digital infrared Swisstec detector with signal processing via AMASIC dedicated chip, triplex optics with black mirror and resistance to small animals up to 40 kg; Actual compensation of temperature change; Built-in filter of white light; Completely protected from penetration of insects and electromagnetic influences; Detection area 12m x 12m; Four levels of sensitivity; Operating temperature -20 ° C to + 50 ° C, IP41 protection category; Ultra low consumption of 6mA |  |  |  | 0
0
3. | MK340-5W | MK340-5W Magnetni kontakt/ MK340-5W Magnetic contact | kom./pcs | 10 | x | 0 | 0
|  | Magnetni kontakt bijele boje, sa 5m kable, 4-žice, okruglog preseka/ Magnetic white contact, with 5m cable, 4-wires, round cross section |  |  |  | 0
| MK300-11W | MK300-11W Montažni set/MK300-11W Mounting set | kom./pcs | 10 | x | 0 | 0
|  | Montažni set za MK340, za instalaciju u okvir vrata, za drvena ili aluminijumska vrata, 1 par/Mounting kit for MK340, for installation in door frame, for wood or aluminum doors, 1 pair |  |  |  | 0
0
4. | MKK2 | MKK2 Magnetni kontakt/MKK2 Magnetic contact | kom./pcs | 10 | x | 0 | 0
|  | Magnetni kontakt za nadzor otvorenosti vrata, za teška gvozdena vrata/Magnetic door opener access control, for heavy iron door |  |  |  | 0
| MKM2 | MKM2 Magnetni kontakt/MKM2 Magnetic contact | kom./pcs | 10 | x | 0 | 0
|  | Stalni magnet, ide u kompletu sa MKK2/Permanent magnet, in set with MKK2 |  |  |  | 0
0
5. | ND100 | ND100 Panic button | kom./pcs | 11 | x | 0 | 0
|  | The ND 100 panic button is used for unobtrusively and manually triggering alarms at work places that are in potential danger of being held up, such as banks, jewelry, shops, businesses, private households etc. |  |  |  | 0
0
6. | FK 32 | Alarmna panik šina/Panic rail alarm | kom./pcs | 11 | x | 0 | 0
|  | Nožna nagazna šina za nečujno aktiviranje alarma, specijalnog dizajana koji onemogućava slučajno aktiviranje, sabotažno zaštićena, sa ručnim resetom/Foot step rail for silent alarm activation, special design that prevents accidental activation, sabotage protected, with manual reset |  |  |  | 0
| FKZ3 | Z-nosač/Z-carrier | kom./pcs | 11 | x | 0 | 0
0
7. | SPCE652.100 | SPCE652.100 X-bus ulazno izlazni modul sa tamperom na poleđini/SPCE652.100 X-Bus Input Output Module with a tamper on the back | kom./pcs | 17 | x | 0 | 0
|  | Ulazno/izlazni modul za proširenje kapaciteta centralnog uređaja preko X-Busa, sa 8 programabilnih nadziranih zonskih ulaza i 2 relejna izlaza; U plastičnom kućištu sa prednjim i zadnjim tamper kontaktom./Input / Output Module to Expand the Capacity of a Central Unit via an X-Bus, with 8 Programmable Controlled Zone Inputs and 2 Relay Outputs; In the plastic case with front and rear tamper contact. |  |  |  | 0
0
8 | SPC6330.310-L1 Intrusion CP,G3 | SPC6330.310-L1 Centralni uređaj/Central Device Sintony Intrusion CP,G3 | kom./pcs | 1 | x | 0 | 0
|  | Centralni uređaj Sintony SPC6330.310-L1 kombinuje u sebi sistem za dojavu provale i sistem kontrole pristupa, može se u skladu sa potrebama proširiti do maksimalno: 512 zona (8 na osnovnoj ploči); 512 programabilnih izlaza (6 na ploči); 32 upravljačke konzole i 64 vrata; Centralni uređaj ima 2 X-BUS porta, podržava do 60 particija, 2500 korisnika; Memorija za 20000 događaja; Integrisan WEB server; 2 terminala za priključenje opcionih GSM i PSTN komunikatora; Ethernet port na ploči; Sistem se može proširiti bežičnim ekspanderima i zonama do ukupnog kapaciteta od 120 bežičnih zona; U kompletu sa napojnim modulom i sa mestom za baterije od 17 Ah i 4 ekspandera u kućištu; U velikom metalnom kućištu sa vratima za nazidnu montažu;/The Sintony SPC6330.310-L1 central unit combines a burglar alarm system and access control system that can be expanded to the maximum: 512 zones (8 on the base board); 512 programmable outputs (6 on board); 32 control consoles and 64 doors; The central unit has 2 X-BUS ports, supports up to 60 partitions, 2500 users; Memory for 20000 events; Integrisan WEB server; 2 terminals for connecting optional GSM and PSTN communicators; Ethernet port on board; The system can be expanded by wireless expanders and zones up to a total capacity of 120 wireless zones; Supplied with power supply module with battery capacity of 17 Ah and 4 expander housings; In a large metal housing with a door for the rear mounting; |  |  |  | 0
| Baterija/Battery | Baterija 12V17Ah/ Battery 12V17Ah | kom./pcs | 1 | x | 0 | 0
0
9. | SPCK620.100 | SPCK620.100 LCD Konforna upravljačka konzola/SPCK620.100 LCD Conformal control console | kom./pcs | 1 | x | 0 | 0
|  | Upravljačka konzola sa LCD displejom veličine 70x40mm (128 x 64 piksela); tasteri sa plavim pozadinskim osvetljenjem; numerička tastatura, navigacioni taster i 4 programabilna dugmeta; praktično neograničen broj informacija; Mogućnost postavljanja logoa na displej; terminali za povezivanje na X-BUS; Standard EN50131-1 / EN50131-3, Grade 3, Class II/ Control console with 70x40mm (128 x 64 pixels) LCD display; blue background illuminators; numeric keypad, navigation keypad and 4 programmable buttons; virtually unlimited number of information; Possibility of placing the logo on the display; terminals for connecting to X-BUS; Standard EN50131-1 / EN50131-3, Grade 3, Class II |  |  |  | 0
0
10 | JH(St)H 3x2x0.8 | Isporuka i polaganje instalacionog kabla bez halogenih elemenata, tipa JH(St)H 3x2x0.8mm/Delivery and installation of installation cable without halogen elements, type JH (St) H 3x2x0.8mm | m. | 1200 | x | 0 | 0
0
11 |  | Isporuka i polaganje rebrastog creva precnika fi 16mm, bezhalogeno/Delivery and laying of corrugated tube in diameter 16mm, non-halogen | m. | 1200 | x | 0 | 0
0
12. |  | Montaza opreme u polju: detektora, koncentratora…/Assembly of equipment in the bay: detectors, concentrators | kom./pcs | 102 | x | 0 | 0
0
13. |  | Programiranje centranog uredjaja, dodavanje novih elemenata, unosenje korisnickih tekstova, primopredaja dokumentacije, obuka korisnika/Programming Center Devices, Adding New Items, Entering User Texts, Delivering Documentation, User Training Programming Center Devices, Adding New Items, Entering User Texts, Delivering Documentation, User Training | paus./lump sum | 1 | x | 0 | 0
UKUPNO DOJAVA PROVALE BEZ PDV-a/TOTAL BURGLAR ALAM, WITHOUT VAT | [6 empty] | 0
PDV/VAT |  |  |  | 21% |  |  | 0
UKUPNO DOJAVA PROVALE SA PDV-om/TOTAL BURGLAR ALAM, WITH VAT | [6 empty] | 0

## 4. Kontrola pristupa_access con
SISTEM ZA KONTROLU PRISTUPA/ACCESS CONTROL SYSTEM
Projekat/Project: |  | Aerodrom Tivat - Novi terminal/Airport Tivat – New Terminal
Br. /No. | Oznaka/Code | Naziv/ Title |  | Kol./Quantity |  | Jed.cena/Unit Price | Ukupna cena/ Total Price
1. | AC5102 | AC5102 Napredni centralni kontroler/AC5102 Advanced central controller | kom./pcs | 1 | x |  | 0
96 vrata, 1.000.000 kartica, komunikacija sa serverom preko LAN mreže, 6 x RS485 za povezivanje lokalnih modula, Sabotažni ulaz, Alarmni izlaz, napajanje 24 VDC/96 ports, 1,000,000 cards, server-to-LAN communication, 6 x RS485 for connecting local modules, Sabotage Input, Alarm output, 24 VDC power supply
Svaki FLN podržava do 16 uređaja, AC5102 ima diagnostic port za direktnui konekciju sa mikroprocesorskim kontrolerom, ima ugrađen RJ45 port za IP komunikaciju, poseduje tamper kontakt za nadzor otvorenosti glavno ormana, kompatibilan sa postojećim sistemom Sipass Integrated, podržan sa verzijom softvera 2.65/Each FLN supports up to 16 devices, AC5102 has a diagnostic port for direct connection with microprocessor controller, a built-in RJ45 port for IP communication, possesses tamper contact to control the openness of the main cabinet, compatible with the existing system SiPass Integrated, supported with software version 2.65
| ENC-020 | ENC-020 Namenski orman za kontrolu pristupa, dimenzija 672x480x122mm/ENC-020 672x480x122mm Dedicated cabinet for access control, dimensions 672x480x122mm | kom./pcs | 1 | x |  | 0
| SV24V150W | SV24V150W Power supply external equipment 24V/150W | kom./pcs | 1 | x |  | 0
| Baterije/Batteries | Aku baterije 12V 27Ah/Batteries 12V 27Ah | kom./pcs | 2 | x |  | 0
2. | PSU | Dodatni napojni modul koji se sastoji od/An additional power module consisting of:
| ENC-020 | ENC-020 Namenski orman za kontrolu pristupa, dimenzija 672x480x122mm/ENC-020 Dedicated cabinet for access control, dimensions 672x480x122mm | kom./pcs | 1 | x |  | 0
| SV24V150W | SV24V150W Power supply external equipment 24V/150W | kom./pcs | 1 | x |  | 0
| Baterije/Batteries | Aku baterije 12V 27Ah/Batteries 12V 27Ah | kom./pcs | 2 | x |  | 0
3. | ADD5160 | ADD5160 Dualni interfejsni modul (DRI), u IP66 kućištu sa uvodnicama, kompatibilan sa postojecim sistemom Sipass Itegrated/ADD5160 Dual Interface Module (DRI), in IP66 housing with slots, Compatible with Existing System Sipass Itegrated | kom./pcs | 10 | x | 0 | 0
Podržava kombinaciju ulazni/Izlazni čitač ili dva nezavisna čitača, relejni izlaz za bravu, ulaz za REX taster, 3 dodatna ulaza, ulaz za nadzor vrata, dodatni relejni izlaz, LED diode za nadzor stanja, 12-32Vdc napajanje,/Supports a combination of an input / output reader or two independent readers, a relay output for the lock, REX button input, 3 additional inputs, gate control input, additional relay output, LED status diode, 12-32Vdc power,
RS485 veza ka ACC kontrolerima; Jedan RS485 bus za do dva RS485 čitača sa CerPass protokolom; ILI dva Wiegand/Clock&Data porta za druge čitače; Podržava konfiguraciju sa ulaznim / izlaznim čitačima ili dva nezavisna čitača; Nadzirani izlazi: relejni izlaz za bravu (30 VDC‚ 2 A), dodatni relejni izlaz (30 VDC‚ 2 A); Nadzirani ulazi: jedan za REX taster, jedan za magnetni kontakt na vratima; 3 dodatna ulaza, LED diode za nadzor stanja (Napajanje, Aktivnost, Komunikacija); U IP66 kućištu od ABS plastike 180 x 180 x 60 mm sa setom od 9 uvodnica; Potrebno je eksterno napajanje 24VDC ±20 % Power output: Reader: 300 mA Ancillary: 1 A/ RS485 connection to ACC controllers; One RS485 bus for up to two RS485 readers with CerPass protocol; OR two Wiegand / Clock & Data ports for other readers; Supports configuration with input / output readers or two independent readers; Supervised outputs: relay output for the lock (30 VDC, 2 A), additional relay output (30 VDC, 2 A); Supervised inputs: One for the REX button, one for magnetic contact on the door; 3 additional entrances, LEDs for status monitoring (Power, Activity, Communication); In IP66 ABS plastic housing 180 x 180 x 60 mm with set of 9 slots; External power required 24VDC ± 20% Power output: Reader: 300 mA Ancillary: 1 A
4. | AR6181-MX | AR6181-MX Mifare Proksimiti čitač/AR6181-MX Mifare Proxime Reader | kom./pcs | 20 | x | 0 | 0
Očitava Mifare kartice, 13.56 MHz, daljina očitavanja do 7 cm, RS485, Clock/Data, Wiegand interfejs, kategorija zaštite IP65, mogućnost očitavanja informacija u sektorima/blokovima kartice/Reading Mifare cards, 13.56 MHz, reading distance up to 7 cm, RS485, Clock / Data, Wiegand interface, IP65 protection category, readability information in card sectors / blocks
5. | Kartica/card | Beskontaktna kartica, Mifare, prazna/Non-contact card, Mifare, empty | kom./pcs | 100 | x | 0 | 0
| EffEff 1334 - - - - E10 | EffEff 1334 - - - - E10 Taster za deblokiranje električnog prihvatnika u slučaju opasnosti, za nazidnu montažu, sa zaštitnim staklom, sa LED indikatorom/ Effeff 1334 - - - - E10 button for unblocking of electrical receptacle in case of danger, for concealed installation, with protective glass, with LED indicator | kom./pcs | 10 | x | 0 | 0
| MAG-05000ALS--HD | MAG-05000ALS--HD Standard Magnet 5000N, koji drži vrata zabravljena u zatvorenom položaju. Napajanje magneta je 24Vdc, sila držanja 5000N, sa senzorom zabravljenosti./MAG-05000ALS - HD Standard Magnet 5000N, holding the door locked in its closed position. The magnet power supply is 24Vdc, holding force 5000N, with locking sensor. | kom./pcs | 10 | x | 0 | 0
| MAGAC-L500 | MAGAC-L500 L-nosač za standard magnet/MAGAC-L500 L-bracket for standard magnet | kom./pcs | 10 | x | 0 | 0
| MAGAC-Z500 | MAGAC-Z500 Z-nosač za standard magnet/MAGAC-L500 L-bracket for standard magnet | kom./pcs | 10 | x | 0 | 0
| MAGAC-M500 | MAGAC-M500 Montažna ploča za standard magnet/MAGAC-M500 Mounting plate for standard magnet | kom./pcs | 10 | x | 0 | 0
| MKK2 | MKK2 Magnetni kontakt/MKK2 Magnetic contact | kom./pcs | 10 | x | 0 | 0
Magnetni kontakt za nadzor otvorenosti vrata, za teška gvozdena vrata/Magnetic contact for door openness control, for heavy iron doors
| MKM2 | MKM2 Magnetni kontakt/MKM2 Magnetic contact | kom./pcs | 10 | x | 0 | 0
Stalni magnet, ide u kompletu sa MKK2/Permanent magnet, in set with MKK2
| DC 240 | Abloy DC240 Hidraulički zatvarač vrata/Abloy DC240 Hydraulic Door Lock | kom./pcs | 10 | x | 0 | 0
| DC103 | Abloy DC103 Montažna ploča /Abloy DC103 Mounting plate | kom./pcs | 10 | x | 0 | 0
0
| ASE5100-DO | ASE5100-DO SiPass dodatna softverska licenca - vrata/ASE5100-DO SiPass additional software license - the door | kom./pcs | 3 | x | 0 | 0
proširenje baze podataka za 8 vrata/database extension for 8 doors
| ASE5300-GP | ASE5300-GP SiPass dodatna softverska licenca, grafički paket/ ASE5300-GP SiPass additional software license, graphic package | kom./pcs | 1 | x | 0 | 0
omogućava operateru metod vizuelnog nadzora sistema, izvršavanje rutinskih zadataka klikom na miš, sveobuhvatna biblioteka simbola, podrška za više od 30 tipova grafičkih fajlova uključujući i AutoCAD / Allows the operator a method of visual monitoring of the system, performing routine tasks by clicking on the mouse, a comprehensive symbol library, support for more than 30 types of graphic files including AutoCAD
| ASL5000-SE | Licenca za upgrade postojece verzije na verziju 2.65 ili noviju, radi kompatibilnosti sa generacijom kontrolera AC5102/ License to upgrade the current version 2.65 or later, for compatibility with AC5102 generation controller | kom./pcs | 1 | x | 0 | 0
Instalacije i radovi/Installations and works
| JH(St)H 3x2x0.8 | Isporuka i polaganje instalacionog kabla bez halogenih elemenata, tipa JH(St)H 3x2x0.8mm/ Delivery and installation of installation cable without halogen elements, type JH (St) H 3x2x0.8mm | m. | 400 | x | 0 | 0
| JH(St)H 5x2x0.8 | Isporuka i polaganje instalacionog kabla bez halogenih elemenata, tipa JH(St)H 5x2x0.8mm/ Delivery and installation of installation cable without halogen elements, type JH (St) H 5x2x0.8mm | m. | 400 | x | 0 | 0
| Box | Montazna kutija za spjeve na jednim vratima/ Mountable box for joints on one door | kom./pcs | 10 | x | 0 | 0
|  | Isporuka i polaganje rebrastog creva precnika fi 16mm, bezhalogeno/ Delivery and laying of corrugated tube 16mm in diameter, non-halogen | m. | 800 | x | 0 | 0
|  | Montaza i povezivanje opreme u polju: kontrolera, citaca, opreme na vratima, tastera…/Assembly and connecting equipment in the field: controllers, readers, door equipment, pushbuttons … | kpl./ set | 70 | x | 0 | 0
|  | Programiranje centranog uredjaja, dodavanje novih elemenata, unosenje korisnickih tekstova, dodavanje potrebnih licenci, prosirenje baze, primopredaja dokumentacije, obuka korisnika/Programming Center Devices, Adding New Items, Entering User Texts, Adding Required Licenses, Expanding Base, Receiving Documentation, User Training | paus./ lump sum | 1 | x | 0 | 0
UKUPNO KONTROLA PRISTUPA BEZ PDV-A/TOTAL ACCESS CONTROLS WITHOUT VAT | [6 empty] | 0
PDV/VAT |  |  | 21% |  |  |  | 0
UKUPNO KONTROLA PRISTUPA SA PDV-OM/TOTAL ACCESS CONTROLS WITH VAT | [6 empty] | 0

## 5. Video nadzor_video surv
SISTEM VIDEO NADZORA/VIDEO SURVEILLANCE SYSTEM
Projekat:/Project: |  | Aerodrom Tivat - Novi terminal/Airport Tivat - New Terminal
Br. /No. | Oznaka/Code | Naziv/ Title |  | Kol./Quantity |  | Jed.cena/Unit Price | Ukupna cena/ Total Price
1. | Outdoor | Isporuka i montaža kolor IP kamere za spoljašnju ugradnju u kompletu sa CS-mount sočivom 5-50mm, kućištem u IP67 zaštiti i grejačem, sl. tipu DALLMEIER sledećih karakteristika: 1/2.5" 5-megapiksela CMOS senzor sa Cam_inPIX® tehnologijom, osetljivost 0.59 lux (at F0.95, 50 IRE), Full HD video u realnom vremenu (1080p/30ips), rezolucija HD HD (720p, 1080p, 2MP, 3MP, 4MP, 5MP), video kompresija H.264, MJPEG, istovremena tri IP stream-a, Automatski balans bele boje (ATW, One-Push AWB), Automatska kontrola pojačanja (AGC); IP67; Napajanje 12Vdc/PoE. /Supply and installation of color IP cameras for exterior mounting, complete with CS-mount 5-50mm lens, housing with IP67 protection and heater, similar to DALLMEIER, with the following features: 1 / 2.5 "5-megapixel CMOS sensor with Cam_inPIX® technology, sensitivity 0.59 (1080p / 30ips), HD HD resolution (720p, 1080p, 2MP, 3MP, 4MP, 5MP), H.264 video compression, MJPEG, simultaneous three (at F0.95, 50 IRE) IP Stream, Automatic Color Balance (ATW, One-Push AWB), Automatic Gain Control (AGC), IP67, 12Vdc / PoE Power. | kom./pcs | 16 | x | 0 | 0
2. |  | Korektivni nosač za montažu klasičnog nosača na fasadu objekta/Corrective bracket for mounting a classic bracket on the façade of the building | kom./pcs | 16 | x | 0 | 0
2. | Indoor | Isporuka i montaža kolor IP kamere za unutrašnju ugradnju u kompletu sa CS-mount sočivom 5-50mm, sl. tipu DALLMEIER sledećih karakteristika: 1/2.5" 5-megapiksela CMOS senzor sa Cam_inPIX® tehnologijom, osetljivost 0.59 lux (at F0.95, 50 IRE), Full HD video u realnom vremenu (1080p/30ips), rezolucija HD HD (720p, 1080p, 2MP, 3MP, 4MP, 5MP), video kompresija H.264, MJPEG, istovremena tri IP stream-a, Automatski balans bele boje (ATW, One-Push AWB), Automatska kontrola pojačanja (AGC); Napajanje 12Vdc/PoE. /Delivery and installation of a color IP camera for indoor installation complete with a 5-50mm D-shaped mount, DALLMEIER, with the following features: 1 / 2.5 "5-megapixel CMOS sensor with Cam_inPIX® technology, sensitivity 0.59 lux (at F0.95, 50 IRE), full HD video (1080p / 30ips), HD HD resolution (720p, 1080p, 2MP, 3MP, 4MP, 5MP), H.264 video compression, MJPEG, three IP streams simultaneously, Auto Balance (ATW, One-Push AWB), Automatic Gain Control (AGC), Power Supply 12Vdc / PoE. | kom./pcs | 36 | x | 0 | 0
3. | PTZ | Isporuka i montaza unutrasnje PTZ kamere, sl. tipu DALLMEIER Full HD video u realnom vremenu (1080p/30ips), rezolucija HD HD (720p, 1080p, 2MP, 3MP, 4MP, 5MP), video kompresija H.264, MJPEG, istovremena tri IP stream-a, /Delivery and installation of an indoor PTZ camera, such as DALLMEIER Full HD video in real time (1080p / 30ips), HD resolution (720p, 1080p, 2MP, 3MP, 4MP, 5MP), H.264 video compression, MJPEG, 3 concurrent IP streams. | kom./pcs | 3 | x | 0 | 0
4. | Ruckus 7150 | L2+ 24-Port 10/100/1000T 802.3at POE+ plus 4-port 10G SFP+ Managed Switches with Hardware Layer3 IPv4/IPv6 Static Routing, 370 POE Budget, ERPS Ring/L2+ 24-Port 10/100/1000T 802.3at POE+ plus 4-port 10G SFP+ Managed Switches with Hardware Layer3 IPv4/IPv6 Static Routing, 370 POE Budget, ERPS Ring | kom./pcs | 3 | x | 0 | 0
| SFP | 1000BASE-SX SFP for Single mode Fiber only | kom./pcs | 6 | x | 0 | 0
| SOCAMCS100 | SOCAMCS100 SeeTec Cayuga S100 prosirenje postojeceg sistema za jedno kamerno mesto/SOCAMCS100 SeeTec Cayuga S100 Expanding the existing system for one camera position | kom./pcs | 55 | x | 0 | 0
Live View, Archive View, Alarm Recording, PTZ Control, Web Client, Mobile Client, Remote Client, Anywhere (Viewer, Client), Redundant System Management Display Agent, SDK, Maps/Floor Plans, Advanced Alarm Scenarios, Encrypted Transmission, Motion Scrambling, Multi Installation Login, Virtualization /Windows Cluster ,Server-based Movement Detection
Analytics (optional) BASIC, Counting (optional), LPR (optional), Analytics Interface, Access Control Integration, Intrusion Detection Integration, Intercom Integration
| Ruckus 7150 | 24portni gigabitni switch u postojećem dijelu objekta povezan putem optike sa switchevima u novoj terminalnoj zgradi 24P, 4xSFP, 370W/24-port Gigabit switch in the existing part of the facility connected via optics with switches in the new terminal building 24P, 4xSFP, 370W | kom./pcs | 1 | x | 0 | 0
| SFP | 1000BASE-SX SFP for Single mode Fiber only | kom./pcs | 2 | x | 0 | 0
| Server | Brandname HP'DJ180 ili sličan server za snimanje video materijala, 12TB Raid5/Brandname HP'DJ180 or similar video recording server, 12TB Raid5 | kom./pcs | 1 | x | 0 | 0
| Radna stanica/workstation | Radna stanica brandname za reprodukciju H.264 streamova, grafika dual head, za jedan monitor i jedan profesonalni displej/Workstation brandname for playback of H.264 streams, dual head graphics, one monitor and one professional display | kom./pcs | 2 | x | 0 | 0
| Monitor | Monitor LED 24" | kom./pcs | 2 | x | 0 | 0
|  | Profesionalni displej za montazu na zid 50"/Professional Wall Mount Display 50 " | kom./pcs | 2 | x | 0 | 0
| Radovi/works | Montaza opreme u polju/Mounting equipment in the bay | kom./pcs | 55 | x | 0 | 0
|  | Montaza centralne opreme/Assembly of central equipment | kom./pcs | 5 | x | 0 | 0
|  | Programiranje serverskih snimaca, dodavanje novih kamera, unosenje korisnickih tekstova, dodavanje potrebnih licenci, primopredaja dokumentacije, obuka korisnika/Programming server recordings, adding new cameras, entering user texts, adding necessary licenses, sending and receiving documentation, user training | paus./lump sum | 1 | x | 0 | 0
UKUPNO VIDEO NADZOR BEZ PDV-A/TOTAL VIDEO SURVEILLANCE WITHOUT VAT | [5 empty] | EUR | 0
PDV/VAT |  |  | 21% |  |  | EUR | 0
UKUPNO VIDEO NADZOR SA PDV-OM/TOTAL VIDEO SURVEILLANCE WITH VAT | [5 empty] | EUR | 0

## 6.Sistem razglasa_Loudspeaker s
SISTEM OPŠTEG I ALARMNOG RAZGLASA/GENERAL AND ALARM LOUDSPEAKER SYSTEM
Projekat/Project: |  | Aerodrom Tivat - Novi terminal/Airport Tivat – New Terminal
Br. /No. | Oznaka/Code | Naziv/ Title |  | Kol./Quantity |  | Jed.cena/Unit Price | Ukupna cena/ Total Price
1. | DOM 4-24 | Centralni uređaj DOM4-24/Central device DOM4-24 | kom/pcs | 2 | x |  | 0
Digitalni kontrolni modul DOM 4-24. Sledećih karakteristika ili boljih: 4 nezavisna digitalna audio linka i kontrola nad maksimalno 24 zvučničke zone. Podešavanje jačine svakog ulaza i kanala pojačavača; 2 NF i kontrolna izlaza za pojačavač; 2 NF i kontrolna izlaza za pojačavač;4 ulaza sa pojačavača i 4 rezervna ulaza sa pojačavača; Nadgledanje svih pojačavača; automatsko i dinamičko prebacivanje na redundantno pomoćno pojačavača u slučaju otkaza; Nadgledanje zvučničkih zona i otkačinjanje u slučaju greške ili poremećaja, bez uticaja na ostatak sistema; Memorija za smeštanje minimalno 4 minuta snimljenih obaveštenja i signala upozorenja za reprodukciju u slučaju alarma; Minimalno 8 programabilnih beznaponskih relejnih izlaznih upravljačkih kontakata; Minimalno 2 10/100Mb/s Ethernet porta za komunikaciju sa drugim kontrolerima i komponentama sistema; Komplet priključnih kablova (za vezu sa ulazima i izlazima pojačavača, za 24 100V linije, za vezu sa LAN svičem); Opremljen za montažu u 19" rek (483mmx44mmx345mm); Napajanje 230VAC/50Hz ProCodex - Honeywell DOM 4-24/ Digital Control Module DOM 4-24. The following features or better: 4 independent digital audio links and control over up to 24 loudspeaker zones. Adjusting the strength of each input and amplifier channel; 2 NF and control output for amplifier; 2 NF and control output for the amplifier, 4 inputs from the amplifier and 4 spare inputs from the amplifier; Monitoring of all amplifiers; automatic and dynamic switching to redundant auxiliary amplifier in case of failure; Spectrum Zone monitoring and failure in case of failure or disturbance without affecting the rest of the system; Memory for a minimum of 4 minutes of recorded information and a warning signal for playback in case of an alarm; Minimum 8 programmable no voltage relay relay output control contacts; Minimum 2 10 / 100Mb / s Ethernet ports for communication with other controllers and system components; Cable connection kit (for connection to the inputs and outputs of the amplifier, for 24 100V lines, for LAN connection); Equipped for mounting in 19 "reck (483mmx44mmx345mm); Power supply 230VAC / 50Hz ProCodex - Honeywell DOM 4-24
2. | 2XD400 | Pojačavač 2X400/Amplifier 2X400 | kom/pcs | 4 | x |  | 0
Power Amplifier 2XH250 sa 2 nezavisna pojačavačka kanala, izlazne snage 2 x 250W za 100V sistem: Frekventni prenosni opseg 20Hz-22kHz ili bolji; 2 NF i kontrolna ulaza sa kontrolera; Elektronska zaštita od pregrevanja i kratkog spoja na izlazu; Opremljen za montažu u 19" rek. Napajanje 230VAC/50Hz. ProCodex - Honeywell 2xD400 = 2 x 400W/ Power Amplifier 2XH250 with 2 independent amplifier channels, output power 2 x 250W for 100V system: Frequency range 20Hz-22kHz or better; 2 NF and control inputs from the controller; Electronic shielding and short-circuit protection at the outlet; Equipped for mounting in 19 "power supply 230VAC / 50Hz. ProCodex - Honeywell 2xD400 = 2 x 400W
3 | UIM | Universal Interface Module (UIM) | kom/pcs | 1 | x |  | 0
Ulazno izlazni modul za vezu sa ostalim sistemima/Input Output Module for Connection with Other Systems
4 | MP02 | Tuner/CD/MP3 Player MP02 | kom/pcs | 1 | x |  | 0
Integrisani DVD / CD plejer, MP3 plejer i FM / AM tjuner, kao i USB / SD čitač. Uređaj podržava dva načina rada. Način rada 1: DVD / USB / SD i FM / AM tjunerom se može upravljati istovremeno preko dva odvojena porta. Način rada 2: DVD / USB / SD i FM / AM tjuner se uključuju i isključuju naizmenično. Izabrani signal se prenosi preko zajedničkog porta. Podržani su DVD video i JPEG formati. Sa Honeywell Esser sistemom se povezuje preko činč audio veze. Pogodno za 24-časovni rad. Dva nezavisna audio izlaza za DVD / USB / SD i FM / AM tjuner Mogu se podesiti dve nezavisne jačine zvuka Kombinovani audio izlaz Radni napon 230 V AC Izlazni napon 2 V DC ± 0,2 V Potrošnja 13 W Ulazi FM 75 Ω, USB-Port, SD-Port Izlazi 1 x činč za FM / AM-Tjuner, 1 x činč za DVD / USB / SD, 1 x činč za mešovite signale Sličan tipu Honeywell Esser X-MAP04. ProCodex - Dual - Honywell MP3/SD/USB/FM - New/ Integrated DVD / CD player, MP3 player and FM / AM tuner as well as USB / SD reader. The device supports two modes of operation. Mode 1: The DVD / USB / SD and FM / AM tuner can be operated simultaneously via two separate ports. Mode 2: The DVD / USB / SD and FM / AM tuners are switched on and off alternately. The selected signal is transmitted over a common port. DVD video and JPEG formats are supported. With the Honeywell Esser system, it connects via the audio link. Suitable for 24-hour work. Two independent audio outputs for DVD / USB / SD and FM / AM tuner Two independent volume outputs Combined audio output Operating voltage 230 V AC Output voltage 2 V DC ± 0.2 V Power consumption 13 W Inputs FM 75 Ω, USB port, SD-Port Outputs 1 x chopper for FM / AM-Tuner, 1 x DVD / USB / SD holder, 1 x clamp for mixed signals Similar to Honeywell Esser X-MAP04. ProCodex - Dual - Honywell MP3 / SD / USB / FM - New
5. | PSU | Jedinica napajanja 24V/100A. 230 V AC, 24V DC, dimenzije 483x133x395 (ŠxVxD) (3HU, 19”). Zajedno sa baterijom 2x 12V/105Ah. ProCodex - Honeywell UPS EN54 + 2 x 105Ah/ Power supply unit 24V / 100A. 230 V AC, 24V DC, dimensions 483x133x395 (WxHxD) (3GB, 19 ") Together with battery 2x 12V / 105Ah.ProCodex - Honeywell UPS EN54 + 2 x 105Ah | kom/pcs | 1 | x |  | 0
6. | DCS15 | Mikrofon DCS15/Microphone DCS15 | kom/pcs | 14 | x |  | 0
Digitalna pozivna stanica DCS15 za selekciju zvučničke linije i emitovanje glasovnih poruka: Mikrofon i minimalno 12 programabilnih tastera; 24-bitna AD/DA konverzija; Digitalna komunikacija audio i kontrolnih signala sa lokalnim kontrolerom sistema javnog razglasa; Mogućnost proširenja na 120 tastera dodavanjem digitalnih tastatura; Audio ulaz za priključenje eksternog izvora zvuka i audio izlaz za priključenje uređaja za snimanje; Kabl F/FTP za vezu sa kontrolerom; Kontrola i napajanje 24VDC sa kontrolera preko digitalne veze./ Digital Calling Station DCS15 for Speakerphone Selection and Voice Messaging: Microphone and minimum 12 programmable keys; 24-bit AD / DA conversion; Digital communication of audio and control signals with the local Public Speaker System Controller; Possibility of extending 120 keys by adding digital touchscreens; Audio input for connecting an external audio source and audio output for connecting to a recording device; F / FTP cable for connection to the controller; 24VDC control and power supply via digital connection controller.
7. | Loc IZ | MP3 lokalni izvor zvuka Ulazni napon 230 V AC Potrošnja 13 W WiFi povezivanje Android OS: Izlaz 1 x 3,5mm stereo; Touch MP3 player 7"/ MP3 Local Sound Source Input voltage 230 V AC Consumption 13 W WiFi connection Android OS: Output 1 x 3.5mm stereo; Touch MP3 player 7 " | kom/pcs | 1 | x |  | 0
8. | DL-A 10-165/T-EN54 | Zvučnik DL-A 10-165/T-EN54 za nadgradnu montažu na plafon/zid sa transformatorskim izvodima 10W/6W/3W/1,5W za priključenje na 100V liniju. (EOL) ProCodex - Honeywell 6a 6W/3W/1,5W/0,75W/ DL-A 10-165 / T-EN54 speaker for wall mounted ceiling / wall mounting with 10W / 6W / 3W / 1.5W transformer output for 100V line connection. (EOL) ProCodex - Honeywell 6A 6W / 3W / 1,5W / 0,75W | kom/pcs | 0 | x |  | 0
| EDL 10-165/T plus/2 | Zvučnik EDL 10-165/T plus/2-ways System za ugradnu montažu u plafon sa transformatorskim izvodima 10W/6W/3W/1,5W za priključenje na 100V liniju. (EOL) ProCodex - Honeywell 48 24W/12W/6W/3W ProCodex - Honeywell LC 6W/3W/1,5W/0,75W/ Speaker EDL 10-165 / T plus / 2-way System for installation in ceiling with transformer outputs 10W / 6W / 3W / 1,5W for connection to 100V line. (EOL) ProCodex - Honeywell 48 24W / 12W / 6W / 3W ProCodex - Honeywell LC 6W / 3W / 1.5W / 0.75W | kom/pcs | 61 | x |  | 0
9. | LIHCH FE180 PH90 2x2.5MM² | Isporuka i polaganje kabla LIHCH FE180 PH90 2x2.5MM²/ Delivery and laying of LIHCH FE180 PH90 2x2.5MM² cables | m | 800 | x |  | 0
|  | Isporuka i polaganje rebrastog creva precnika fi 16mm, bezhalogeno/Delivery and laying of corrugated tube in diameter 16mm, non-halogen | m. | 800 | x | 0 | 0
|  | Set sistemskih kablova i konektora/Set of system cables and connectors | kpl/set | 1 | x | 0 | 0
|  | Montaza opreme u polju/Mounting equipment in the bay | kom/pcs | 61 | x |  | 0
|  | Montaza centralne opreme/ Installation of central equipment | kom/pcs | 8 | x |  | 0
|  | Programiranje i pustanje u rad/Programming and setting into operation | paus./lump sum | 1 | x |  | 0
UKUPNO MM8000 BEZ PDV-A/TOTAL MM8000 WITHOUT VAT | [5 empty] | EUR | 0
PDV/VAT |  |  | 21% |  |  | EUR | 0
UKUPNO MM8000 SA PDV-OM/TOTAL MM8000 WITH VAT | [5 empty] | EUR | 0

## 7. FIDS SISTEM_FIDIS SYSTEM
FIDS SISTEM /FIDS SYSTEM
Projekat/Project: |  | Aerodrom Tivat - Novi terminal/Airport Tivat – New Terminal
Br. /No. | Oznaka/Code | Naziv/ Title |  | Kol./Quantity |  | Jed.cena/Unit Price | Ukupna cena/ Total Price
1. | 43" | Monitor 43" za Digital Signage LG/Monitor 43" FOR Digital Signage LG | kom/pcs | 15 | x |  | 0
LG 43SM5D, 24/7
2. | 65" | Monitor 65" za Digital Signage LG/Monitor 65" for Digital Signage LG | kom/pcs | 10 | x |  | 0
LG 65 SM5D, 24/7
3. | Plejer/Player | Otrum DS HW plejer/Otrum DS HW player | kom/pcs | 25 | x |  | 0
4 | Otrum | Otrum Digital signage redundantni cl.server CMS pristup Postavljanje slika, tekstova, videa sa postojećih računara zaposlenih u Specijalizovani modul za konferencije Automatsko priakazivanje sadržaja, vezano za raspored konferencija Bez ograničenja skladišnog prostora na serveru Konekcija visokog nivoa bezbednosti, stabilan servis. Automatski Management back-up servera, redudantnsot i redovni back-up. Automatski update softvera. Summary ekrani Podeška zbirnih ekrana sa automatskim usmeravanjem gostiju u zavisnosti od događanja u konferencijskim salama./ Otrum Digital signage redundant cl. server CMS Access Set up images, texts, and videos from existing computers in the Specialized Conference Module Automatic content retrieval related to conference scheduling Without server storage space limitations High level security connectivity, stable service. Automatic Management Back-Up Server, Redundancy, and Regular Back-Up. Automatic update software. Summary screens. Support of aggregate screen displays with automatic guiding of guests depending on the events in conference rooms. | kom/pcs | 1 | x |  | 0
5. | Patch | Patch cable 1m | kom/pcs | 50 | x |  | 0
|  | Plafonski/zidni nosač, visina do 1,5m od noseće konstrukcije Kompatibilan sa LG displej Nabavka, Isporuka, Montaža/ Ceiling / wall mount, height up to 1.5m from supporting structure Compatible with LG Displays Purchase, Delivery, Installation | kom/pcs | 25 | x |  | 0
|  | Montaza opreme u polju/Mounting equipment in the bay | kom/pcs | 25 | x | 0 | 0
|  | Montaža centralne opreme/Installation of central equipment | paus./lump sum | 1 | x |  | 0
|  | Programiranje i pustanje u rad/Programming and setting into operation | paus./lump sum | 1 | x |  | 0
UKUPNO FIC SISTEM BEZ PDV-A/TOTAL FIC SYSTEM WITHOUT VAT | [5 empty] | EUR | 0
PDV/VAT |  |  | 21% |  |  | EUR | 0
| UKUPNO/TOTAL | FIC SISTEM SA PDV-om/FIC SYSTEM WITH VAT |  |  |  | EUR | 0

## 8. CSNU
SISTEM ZA CENTRALNI NADZOR I UPRAVLJANJE/CENTRAL SURVEILLANCE AND CONTROL SYSTEM
Projekat/Project: |  | Aerodrom Tivat - Novi terminal/Airport Tivat – New Terminal
Br. /No. | Oznaka/Code | Naziv/ Title |  | Kol./Quantity |  | Jed.cena/Unit Price | Ukupna cena/ Total Price
|  | Licenca za upgrade sistema na verziju MP4.80 kompatibilnu sa Sinteso centralom i Sipass-om Integrated v2.65/System upgrade license for MP4.80 compatible with Sinteso central and Sipass Integrated v2.65 | kpl/set | 1 | x |  | 0
|  | Licencno prosirenje za jedan podsistem/License extension for one subsystem | kom/pcs | 2 | x |  | 0
|  | Licencno prosirenje za 100 fizickih tacaka/License Expansion for 100 Physical Points | kom/pcs | 3 | x |  | 0
|  | Programiranje i pustanje u rad/Programming and setting into operation | kom/pcs | 1 | x |  | 0
UKUPNO MM8000 BEZ PDV-A/TOTAL MM8000 WITHOUT VAT | [5 empty] | EUR | 0
PDV/VAT |  |  | 21% |  |  | EUR | 0
UKUPNO MM8000 SA PDV-OM/TOTAL MM8000 WITH VAT | [5 empty] | EUR | 0

## Rekapitulacija_Recapitulation
REKAPITULACIJA /RECAPITULATION
1 | Sistem sks i wi-fi mreže/Sks and wi-fi network system | 0
2 | Sistem automatske detekcije i dojave pozara/ Automatic fire detection and alarm system | 0
3 | Sistem dojave provale/ Burgler alarms system | 0
4 | Sistem kontrole pristupa/ Access control system | 0
5 | Sistem video nadzora/ Video surveillance system | 0
6 | Sistem za centralni nadzor i upravljanje/ Central surveillance and control system | 0
7 | FIDC sistem/FIDIC system | 0
8 | Sistem razglasa/Loudspeaker system | 0
| Ukupno/ Total | 0
| PDV 21% | 0
| Ukupno sa PDV-om/ Total with VAT | 0

## Rekapitulacija 1_Recap 1
REKAPITULACIJA 1/RECAPITULATION 1
1 | Sistem sks i wi-fi mreže/Sks and wi-fi network system | 0
2 | Sistem automatske detekcije i dojave pozara/ Automatic fire detection and alarm system | 0
3 | Sistem dojave provale/ Burgler alarms system | 0
4 | Sistem kontrole pristupa/ Access control system | 0
6 | Sistem za centralni nadzor i upravljanje/ Central surveillance and control system | 0
7 | FIDC sistem/FIDIC system | 0
| Ukupno/ Total | 0
| PDV/VAT 21% | 0
| Ukupno sa PDV-om/ Total with VAT | 0

## Rekapitulacija 2_Recap
REKAPITULACIJA 2/RECAPITULATION 2
5 | Sistem video nadzora/Video Surveillance System | 0
8 | Sistem razglasa/Loudspeaker system | 0
| Ukupno/Total | 0
| PDV/VAT 21% | 0
| Ukupno sa PDV-om/Total with VAT | 0