BID BULLETIN 2 (Amendment 2) on bid reference ITB-YEM-0037-209.

MINUTES OF MEETING PRE-BID SUBMISSION MEETING

Date: JULY 30,2019 11:00am Sana’a time (GMT+3)

BID Reference: ITB-YEM-0037-2019

Bid Subject: LONG TERM AGREEMENT FOR PROVISION & INSTALLATION OF FULL SOLAR SYSTEMS.

Venue: UNDP Sana’a office

**Presentation of the pre-bid meeting:**

After having companies introduce themselves, the Solar Specialist has given detailed presentation of the **specification for all LOTs. Procurement officer also provided presentation about the tender instructions, conditions and e-tendering system guidelines.**

**Questions and answers:**

**Question 1: Please change the battery bank voltage for LOT 1 item 5 from 48 VDC to 24 VDC?**

**Answer: The bank voltage for item 5 under LOT 1 has been changed to 24 VDC bank voltage.**

**Question 2: Please clarify if the parallel operation is required for all inverters?**

**Answer: The parallel operation is MUST for inverter related to 5.2kw under LOT 6. However, if the bidder proposed the parallel operation for other LOTS also will be acceptable.**

**Question 3: Please clarify if the mounting structure stand capability of wind load 150km/hour is acceptable?**

**Answer: The minimum wind load for mounting structure capability has been changed from 180km/hour to 150km/hour for ALL LOTs. Therefore, the minimum wind load for mounting structure capability is 150km/hour for all LOTs.**

**Question 4: If the bidder submitted only for one LOT is still the bid security amount USD 25,000.00 will remain the same?**

**Answer: Yes the bid security amount will remain the same USD 25,000.00 with 120 days validity period whether the bidder submitted for one LOT or for all LOTs.**

**Question 5: The delivery period mentioned in the tender (6 months) shall apply for all quantities mentioned in the LOTs or for each UNDP request during the LTA period?**

**Answer: The delivery period (6 months) mentioned in the ITB document will apply only in each request which may raise under UNDP Purchase order during the long term (LTA) period. Therefore the bidder shall committed for 6 months delivery period for each PO request despite the number of quantities mentioned in the Purchase order.**

* **Any other bid conditions in the ITB-YEM-0020-2019 documents will remain the same.**

**Sincerely,**

**Procurement unit.**