## Site preparation
S.n. | S.n. | Description | Unit | QTY | Rate in $ | Amount in $
A. |  | Site cleaning preparation activities
1 | 1 | Site cleaning for small trees and sharps
1.1 | 1.1 | Removing of existing old guard shelters made with wooden frame and CGI sheets. Ditto, the temporary toilets at North-West cornice of the compound. The GI sheets and wooden should be handed over to the security staff of the building. The broken materials should be dumped beyond 1.0km from site with approval of district municipality. | Lump Sum | 1 |  | 0
1.2 | 1.2 | Cleaning of existing wild trees and sharps inside of the compound. The rest of broken truck, quarry stones and broken of construction materials from former demolished residences, guard shelters and toilet should be dumped at least 1 km from the site with the permission of Municipality of the district. N.B. Note that the leaves and trunks of removed trees should be cleared properly, otherwise this material can be affected the compaction and lifespan of the building. | Lump Sum | 1 |  | 0
1.3 | 1.3 | Soil movement which consist cutting the top hill and filling the soil removed in to the depressed area in order to have steps as mentioned in the attached “Soil movement for the ground adjustment”. This activity must be used by bulldozer, front loader or other equivalent machine to move the soil. Cutting of the existing the hill at the East side of the road by using bulldozer or other excavator machine. | m³ | 716.19 |  | 0
1.4 | 1.4 | Spreading of removed soil from the mountain area by bulldozer or grader machine. The amount of each layer shall not exceed than 150mm thick. | m³ | 716.19 |  | 0
1.5 | 1.5 | Leveling of spreading of material by grader or equivalent machine. The amount of each layer shall not exceed than 150mm thick. | m³ | 716.19 |  | 0
1.6 | 1.6 | Pouring with water on top of the upper layers of the speeded excavated material by showering slowly with water truck. Note that the watering should be covered the entire area (100mx45m) including the places where removed the hills. | m² | 10800 |  | 0
1.7 | 1.7 | Compaction with watering of the spread soil with layers in which not exceed than 150mm thick each time. The degree of compaction shall be not less than 95% Maximum Dry Density (MDD). Note that the compacting should be used the entire area (100mx45m) including area where removed hills. N.B. This compaction should be use by adequate compactor tractor | m² | 10800 |  | 0
|  | Sub total - 1 |  |  |  | 0
|  | Total for Site cleaning for small trees and sharps |  |  |  | 0

## Retaining wall
S.n. | Description | Unit | QTY | Rate in $ | Amount in $
B. | Construction of retaining wall at north side of the building
2 | Substructure works
2.1 | Excavation of trench of required of 9,100cm length, width 60cm x 110cm deep foundation wall including excavation for sockets and dressing of sides, ramming of the bottoms including getting out the excavated soil and then returning the soil as required in layers not exceeding 20cm in depth including consolidating each deposited layer by ramming watering etc. and disposing of surplus excavated soil as direction by UNDP site engineer within lead of approximately 90m from excavated point. | m³ | 60.06 |  | 0
2.2 | Construction of 5cm thick Plain cement concrete of 1:3:6 mixing of 60cm wide | m³ | 2.73 |  | 0
2.3 | Construction of trapezoid stone wall of 60cm top width, 110cm at bottom width and 250cm height (60cm under ground and 190cm above ground). The foundation walls should be made by rubble stone jointed and connected by cement sand mortar of mixing ratio 1:6 | m³ | 193.375 |  | 0
2.4 | Provide and fixing three lines of PVC pipes of diameter Ø 8cm @ 200cm c/c inside of the retaining stone wall during the construction. | Rods | 42 |  | 0
2.5 | Construct 60cm wide, 20cm thick of reinforced concrete beam of 1:2:4 mixing ratio with # 6 Y16 and staffs of 8mm@ 250mm/cc over the retaining wall | m³ | 10.92 |  | 0
2.6 | Apply 20mm thick and 30mm width pointing plastering with cement sand mortar on 1:5 for external wall surfaces of stone walling. Walls should be cured at least for one week after 24 hours of plastering. | m² | 178.36 |  | 0
| Sub total - 2 |  |  |  | 0
| Total for sitting up and construction of protection hoarding wall |  |  |  | 0

## Setting up
S.n. | Description | Unit | QTY | Rate in $ | Amount in $
C. | Sitting up and construction of protection hoarding wall
3 | Setting up and hoarding wall
3.1 | Providing and fixing of wooden of cross section 20cmx2.5cm at surrounding area of construction site with skeleton poles made by timber of cross section 40cmx80cm and 150cm height (50cm under ground and 100cm above ground level) at 200cm c/c | Item | 1 |  | 0
3.2 | Construction of 17,800cm length and approximately 700cm height hoarding protection at surrounding area of the construction site. This consists wooden structure mounted around the building area covered on it by corrugated iron sheets at the bottom and double layer of PVC nets above the iron sheets, in order to protect the damage causing if any construction materials fall or get broken. This hording is a temporary shelter in which the contractor should include budget of mounting, dismounting and transporting after when the implementation if finished | Item | 1 |  | 0
| Sub total - 3 |  |  |  | 0
| Total for Sitting up and construction of protection hoarding wall |  |  |  | 0

## Data center
S.n. | Description | Unit | QTY | Rate in $ | Amount in $
D. | Construction of Data center hall with screening room and toilets
4 | Substructure works
Excavation and Earthwork (Provisional)
4.1 | Excavation of soft soil for foundation trenches of 60cm wide and 173cm depth starting from stripped level. When construction of foundation finishes, these materials should be returning and filled around foundation, where extra surplus materials must be dumped at least 2km away from the site as per directed by UNDP engineers. | m³ | 106.395 |  | 0
4.2 | Ditto for internal subdivision wall of the toilets and screening room of 40cm wide and 50cm depth. | m³ | 4.24 |  | 0
4.3 | Ditto for column footings of 120cmx120cmx218cm depth. | m³ | 65.9232 |  | 0
| Selected filling |  |  |  | 0
4.4 | Provide and compact 28cm height hardcore layer with approved materials over the existing floor of whole building including the staircase and ramp of the building | m³ | 70.7616 |  | 0
| Anti-termite treatment |  |  |  | 0
4.5 | Provide and apply on the upper surfaces of hardcore layer a chemical spry or powder anti-termite treatment as "Premise 200 SC" or other equal and approved anti insecticide materials. | m² | 252.72 |  | 0
| Damp proof membrane |  |  |  | 0
4.6 | Provide and lay 1000-gauge polythene or other equal and approved damp proof membrane laid under surface bed with 300mm side and end laps (measured net- allow for laps) | m² | 252.72 |  | 0
| Concrete work in substructure |  |  |  | 0
4.4 | Construction of 5cm thick and 60cm wide Plain cement concrete of class 15 ( 1:3:6 mixing) under the foundation walls of the building. | m³ | 3.075 |  | 0
4.5 | Ditto for internal subdivision wall of the toilets and screening room of 40cm wide and 5cm thick. | m³ | 0.424 |  | 0
4.6 | Ditto for column footing of 120cmx120cmx5cm depth. | m³ | 1.512 |  | 0
| Foundation Walling |  |  |  | 0
4.7 | Construction of 40cm wide and 188cm height (168cm under ground and 20cm above ground) foundation wall made by rubble stone jointed and connected by cement sand mortar of mixing ratio 1:6 | m³ | 92.7216 |  | 0
4.8 | Ditto for internal subdivision wall of the toilets and screening room of 40cm wide and 65cm thick. | m³ | 5.4314 |  | 0
| Sub total - 4 |  |  |  | 0
5 | Super structure works
Plain and reinforced concrete works
5.1 | Construct 120cmx120cmx40cm reinforced concrete of 1:2:4 mixing ratio for footing of the columns with 9 numbers of Y16 both ways. | m³ | 12.096 |  | 0
5.2 | Ditto columns neck of 40cm x40cm with 10 numbers of Y 16mm | m³ | 7.0896 |  | 0
5.3 | Construct 40cm wide, 20cm thick of reinforced concrete beam of 1:2:4 mixing ratio with # 8 Y16 and staffs of 8mm@ 250mm/cc over foundation wall including staircase | m³ | 9.864 |  | 0
5.4 | Laying 7cm thick plain cement concrete of 1:3:6 mixing ratio over newly constructed hardcore layer with proper finish. | m³ | 17.6904 |  | 0
5.5 | Construct 17 pieces of 30cm x 40cm reinforced concrete columns of 400cm height of the building. The concrete must be 1:2:4 mixing ratio and reinforced with No. 8 Y16 and staffs of Ø 8mm @250mm c/c. N.B. Note that the columns should be protected from sun and kept moist for at least 10 days. | m³ | 8.16 |  | 0
5.6 | Construct 4 numbers of 400cm height reinforced concrete octagonal shape columns of external diameter not exceed than Ø 48cm decorated on top with Roman architectural and profiled on the sides by 8 longitudinal lines of approximately 3cm deep and 5cm. The concrete must be 1:2:4 mixing ratio and reinforced with No. 8 Y16 and with spiral of diameter Ø 16mm @ 80mm c/c. N.B. Note that the columns should be protected from sun and kept moist for at least 10 days. | m³ | 2.8938 |  | 0
5.7 | Construct 20cm wide, 15cm thick of reinforced concrete 2.2m level beam of 1:2:4 mixing ratio with # 6 Y14 and staffs of 6mm@ 250mm/cc. This is for all constructed walls including toilets and screening room. | m³ | 3.378 |  | 0
5.8 | Construction of reinforced concrete corbel on external top edges of windows. The corbel must be constructed in three steps of 5cm height each with the top layer of 250cmx 70cm, where the second layer is 240cm x 65cm and the last layer at the bottom is 226cmx60cm, with two supporting braces (see detail drawings). The concrete should be mixed by 1:2:4 and reinforced with iron bars of diameter Ø12mm and Ø 10mm | m³ | 2.2158 |  | 0
5.9 | Ditto windows for toilets of 175cm x 70cm, where second layer is 165cm 65cm and third layer of 162cm x 60cm. | m³ | 0.7055 |  | 0
5.1 | Construct of 180 cm x 30 cm x 5cm reinforced concrete window sills at bottom edge windows for offices and toilets. The concrete should be mixed by 1:2:4 with # 3 Y12 and staffs of 8 mm @ 200mm/cc | m³ | 0.297 |  | 0
5.11 | Construction of reinforced concrete 1:2:4 mixing ratio loaded beam of 30cm width and 65cm height (15cm inside of the slab and 50cm outside). The concrete should be reinforced with 6 pieces of straight bars diameter ∅ 16mm (2 on top and 4 at the bottom), 2 pieces of bended bars diameter ∅ 16mm and 2 reinforcement bars of diameter ∅ 16mm of 300cm length on top of the columns. All these bars should be united by staffs of 8mm@ 250mm/cc. N.B. Note that the calculated quantities volume is only the lowest part of the beams (50cmx30cm) as the top part is inside of the slab and will considered part of the slab structure. | m³ | 13.125 |  | 0
5.12 | Construction of reinforced concrete 1:2:4 mixing ratio final beam (Not loaded) of 20cm width and 35cm height (15cm inside of the slab and 20cm outside). The concrete should be reinforced with 6 pieces of bars diameter ∅ 16mm with staffs of iron bars of 8mm@ 250mm/cc | m³ | 2.252 |  | 0
| Sub total - 5 |  |  |  | 0
6 | Construction of steps access
6.1 | For the front access ramp with steps in the middle: Construction of 360cm wide and 600cm length made stone laid and jointed with cement sand mortar of 1:6 mixing. After it poured on top by 10cm thick plain cement concrete of 1:2:4 mixing ratio. Note that this ramp should be kept moist and protect from the sun for at least 10 days. | Item | 1 |  | 0
6.2 | Construction of front staircase of 30cm trade and 15cm rise made by rubble stone jointed and connected with cement sand mortar of 1:6, with 10cm plain cement concrete of 1:2:4 on top of stone base | Item | 1 |  | 0
| Sub total - 6 |  |  |  | 0
7 | Construction of concrete blocks
7.1 | Construction 355cm height for East and West walls and 335cm for North and South walls of masonry cement blocks (0.40mx0.20mx0.20m) wall laid and jointed by cement sand mortar of 1:6 mixing ratio. Note that price will be include reinforcement hoop iron made by fixing of two lines of iron bars of diameter Ø 8mm for every alternate course. N.B. Note that the given height is only the cement blocks wall which is not included the ring beams | m² | 198.35 |  | 0
7.2 | Ditto for the front wall of toilets and screening room walls of 370cm height | m² | 51.84 |  | 0
7.3 | Ditto internal subdivision walls of toilets of 245cm height Note the this dimension is not included the two beams | m² | 30.03 |  | 0
| Sub total - 7 |  |  |  | 0
8 | R.C roofing
8.1 | R.C (1:2:4 Mixing ratio) slab cover of 15cm thick with Ø 12mm main bars and 10mm distribution bars both ways at top and bottom and distanced 15cm c/c .Formwork must be accurately set out, this means when remove the formwork all surfaces should be smooth and NO NEED TO BE PLASTERED, so that the resulting concrete product is in a right place and is of correct shape and size. N.B. The structure should be kept moist and protect from the sun for at least 10days | m³ | 48.3226 |  | 0
8.2 | Construction of 15 numbers of trapezoid shape reinforced concrete braces under the projection of the slab of 25cm thick with top width of 73cm and bottom width of 40cm and 30cm height reinforced with iron bars of diameter Ø16 and staffs of diameter 8mm. | m³ | 0.63562 |  | 0
| Sub total - 8 |  |  |  | 0
9 | Flooring
9.1 | Construction of 60cm x 60cm non slippery ceramic floor tiles for all pavement of the building laid and jointed with cement sand mortar of 1:2 mixing. Note that the price is included the floor hall, toilets and screening room | m² | 283.03 |  | 0
9.2 | Construction of 60cm x 10cm ceramic skirting tiles for all bottom edge of the walls of the building laid and jointed with cement sand mortar of 1:2 mixing. Note that the price is included the skirting tiles of the corridor. | m | 84.1 |  | 0
9.3 | Construction of 60cm x 60cm non slippery local made terrazzo floor on the top surfaces of ramps and step access of the building. The terrazzo should be divided by PVC or steel boundary edges with light green color. Note that the proportion of cement sand must be 1:2 mixing. | Item | 1 |  | 0
9.4 | Construction of ceramic floor marble tiles on the trade and rise of the steps South side of the building. The marble must be laid and jointed with cement sand mortar of 1:2 mixing. The sample of the marble has to be got approved from site engineer before fixing. N.B. Note that the given area is only the trades of staircase of 30cmx120cm, but the bidder should include his/her prices the budget of the rises of 15cmx120cm | m² | 4.32 |  | 0
9.5 | Construction of 140cm width along external edges of the building with floor paving made by cement sand interlocking with all required fitting and fixer such as retaining wall of cement blocks to external edges, aggregate powder to lay the floor before fixing the paving etc. Also the price should be added construction of retaining wall made by cement blocks laid and jointed with cement sand mortar of 1:6 mixing with adequate foundation wall of at least 40cm under ground. | m² | 87.92 |  | 0
| Sub total - 9 |  |  |  | 0
10 | Plastering and other decoration works
10.1 | Apply of first coat on 30mm thick plastering of cement sand mortar of 1:6 mixing ratio for all external new constructed stone wall surfaces | m² | 35.094 |  | 0
10.2 | Apply 20mm thick on internal external plastering with cement sand mortar of 1:5 mixing ratio for all new constructed wall surfaces including stone walls. | m² | 674.456 |  | 0
10.3 | Apply on 10mm thick rough cast plastering of cement sand mortar of 1:2 mixing ratio on external 1,200mm bottom part of the windows sills of wall surfaces including the first floor. Note that the wall should be market by blocks of 52cmx26cm with lines approximately 1cm wide. | m² | 70.188 |  | 0
10.4 | Construction of 270cm height ceramic wall tiles for all walls of the toilets laid and jointed with cement sand mortar of 1:2 mixing | m² | 110.16 |  | 0
10.5 | Apply two coats white wash with white emulsion filler on all wall surfaces, and filling with it on all depressed area of the wall surfaces including the under ceiling with external projection of under ceiling of the slab. | m² | 831.981 |  | 0
10.6 | Apply two coats of light yellow distemper inside and outside of building walls and white distemper on under ceiling | m² | 831.981 |  | 0
10.7 | Apply two coats of light grey distemper paint on the rough casted surfaces at external walls of building. | m² | 70.188 |  | 0
| Sub total - 10 |  |  |  | 0
11 | Electricity
INTERIOR ELECTRICAL SERVICES
Lighting
11.1 | Type F1: 1200mm 1x18w Surface Mounted LED light fitting with CAT 2 Louvered with maximum unified glare of 19 and with LED lamp as "Thomson" LED (1x1750LM MIN)The lamp shall have a minimum of 30,000 hours lifetime; and with 50000 times switching cycles. The color temperature shall be 3000 - 7000K and luminous flux of 1500 - 1700 lumens. | Item | 44 |  | 0
11.2 | Type F1E: Ditto as Type F1 above but emergency version of 3hour duration | Item | 24 |  | 0
11.3 | Type E- 21w IP44 die-cast aluminum light fitting with clear diffuser and complete with lamp as massive Sussex CAT 81657/01/30 | Item | 4 |  | 0
11.4 | Type 4 - 8.5w IP54 LED spherical ball light fitting complete with LED lamps for toilets | Item | 6 |  | 0
11.5 | Type EXIT: 8W, Non-maintained illuminated emergency exit light sign luminaire with white steel body. Emergency lighting of 3 hour duration | Item | 6 |  | 0
| Sub total - 11 |  |  |  | 0
12 | Light Switches
12.1 | Supply, install and connect following 10A lighting switches on recessed switchboxes wired in 1.5 sq.mm PVC single core copper cables enclosed in concealed HG PVC conduits complete with all necessary accessories:
12.2 | 1 gang 1 way | Item | 8 |  | 0
12.3 | 1 gang 2 ways | Item | 5 |  | 0
12.4 | 2 gangs 2 ways | Item | 5 |  | 0
12.5 | 3 gangs 1 way | Item | 1 |  | 0
12.6 | Intermediate switch | Item | 1 |  | 0
| Sub total - 12 |  |  |  | 0
13 | Power sockets, Isolators and DP Switches
13.1 | Supply, install, test and commission the following power sockets as shown on drawing, as per the preamble, the specifications and supervision engineer's requirements.
13.2 | Supply, install and connect 13Amp standard twin socket outlets for normal power as MK or equal and approved (5numbers for each room of 6.2mx3.68m). Note that the sockets must be fixed at least 60cm from the pavement level. | Item | 42 |  | 0
13.3 | Supply, install and connect 13Amp standard twin socket outlets for normal power as MK or equal and approved for the Wi-Fi at the corridor of the building. Note that the sockets must be fixed at least 60cm from the bottom level of concrete slab. | Item | 4 |  | 0
13.4 | Supply, install and connect 15A un-switched DP outlet plate with fuse connector and neon indicator for Fire Alarm Panel power supply and marked "FACP" | Item | 2 |  | 0
13.5 | Supply, install and connect 30A switched TPN industrial isolator outlet plate with connector Split Air Conditioning Units power supply and marked "AIR CONDITIONER" respectively | Item | 24 |  | 0
| Sub total - 13 |  |  |  | 0
14 | Cables, Cable pathways and Conduits
14.1 | Supply, install, test and commission 450/750 volts 6491X cables with all required accessories for proper installation and operation including conduits, pipes( each cable in separate conduit or pipe), cable lugs, ties... etc. as shown on drawing, as per the preamble, the specifications and supervision engineer's requirements.
14.2 | Supply, install and connect complete 3x1.5 sq. mm color-coded SC cables to lighting points drawn in Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 80 |  | 0
14.3 | Supply, install and connect complete 3x2.5 sq. mm color-coded SC cables to lighting points drawn in Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 4 |  | 0
14.4 | Supply, install and connect complete 3x2.5 sq. mm color-coded SC cables to socket power points drawn in ring and within Concealed /surface 25mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 42 |  | 0
14.5 | Supply, install and connect complete 3x2.5 sq. mm color-coded SC cables to Fire Alarm Panel power points drawn in spur and within Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 2 |  | 0
14.6 | Supply, install and connect complete 3x2.5 sq. mm color-coded SC cables for Split Air Conditioning Units power supply drawn in spur and within Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 24 |  | 0
14.7 | Supply and install 4C, 50sq.mm XLPE/SWA /PVC Copper Cable from generator at West side of main entrance gate DB to new building DB' complete with cable lugs and cable glands | m | 200 |  | 0
14.8 | Excavate trench for XLPE/SWA /PVC Copper Cable not exceeding 300 mm and average 500 mm deep, part return, fill in, ram the ground (Final ground finish with direction of site engineer) | m | 170 |  | 0
14.9 | Electrical ducts and manholes |  |  |  | 0
14.1 | Supply and install the following uPVC ducts at 600mm below ground level. Rate to be inclusive of trenching at 600mm below ground level, back filling of trenches, and laying of "DANGER" cable tiling, reinstatement and making of good of ground as per directed by the site engineer: |  |  |  | 0
14.11 | a) 2x100mm uPVC duct | m | 170 |  | 0
14.12 | Construct 600mm x 600mm x 600mm deep [internal dimensions] reinforced concrete power manhole complete with heavy duty cast iron cover | Item | 8 |  | 0
| Sub total - 14 |  |  |  | 0
15 | Distribution Boards
15.1 | Supply, install, connect, testing and commission the following final distribution boards, distribution terminal blocks according to drawings, specifications and relevant codes and as Merlin Gerin or equal and approved
15.2 | Supply, install, connect-up complete 250 Amp 4 way TP/N main Distribution Board as Merlin Gerin or equal and approved for normal power supply, for main DB (UNSOM main switch board at back side of the building) complete with integral isolator, and 3.No 63 Amps MCCBs as specified | Item | 1 |  | 0
15.3 | Supply, install, connect-up complete 100 Amp 6way TP/N MCB Distribution Board as Merlin Gerin or equal and approved for normal power supply, for ground floor complete with integral isolator as specified | Item | 1 |  | 0
15.4 | Supply, install, and connect 100Amp, 4 way SP/N Consumer unit , as Merlin Gerin or approved equivalent, as shown on schematic wiring drawing for lightings load only | Item | 1 |  | 0
15.5 | Supply, install, test and commission miniature circuit breakers (MCBs) rated at 500Vac for above items with 10KA short circuit current according to schematics, specifications and relevant codes and as Merlin Gerin or equal and approved |  |  |  | 0
15.6 | 10A (TP)- 30mA | Item | 1 |  | 0
15.7 | 30A (TP)- 30mA | Item | 25 |  | 0
15.8 | 10A (SPN)- 30mA | Item | 1 |  | 0
15.9 | Blanking plates for items above(TP) | Item | 1 |  | 0
15.1 | Blanking plates for items above(SP) | Item | 1 |  | 0
| Sub total - 15 |  |  |  | 0
16 | Earthling
16.1 | Supply, install, test and commission Copper earthling mat for electrical system of 1200mmx1200mm dimensions constructed of 25mm x 3mm copper tape laid 1000mm deep in ground and complete with 10sq.mm earth lead cable for earthling in Masonry earth pit and with concrete removable cover marked "EARTH" | Lump Sump | 1 |  | 0
16.2 | Allow for testing and commissioning Electrical Installations | Lump Sump | 1 |  | 0
16.3 | FIRE DETECTION AND ALARM SYSTEM |  |  |  | 0
16.4 | Supply and install 1.5mm sq. fire rated copper cable for Smoke detector outlet as per layouts | Item | 12 |  | 0
16.5 | Supply and install 1.5mm sq. fire rated copper cable for Sounder outlet per layouts | Item | 5 |  | 0
16.6 | Supply and install 1.5mm sq. fire rated copper cable for Call point fire break glass unit outlet per layouts | Item | 4 |  | 0
16.7 | Supply and install complete 4-zone conventional fire alarm panel as Menvier MF9304 or equivalent by HF Fire but approved by engineer as per the specifications | Item | 1 |  | 0
16.8 | Supply and install conventional surface mounted Call point fire break glass unit as menvier MBG914 or similar but approved complete with conduit and wiring as shown on the drawings | Item | 4 |  | 0
16.9 | Supply and install conventional optical Smoke Detector / Sensors unit as Menvier MID810 or similar but approved complete with conduit and wiring a shown on the drawings | Item | 12 |  | 0
16.1 | Supply and install 93 mm diameter conventional electronic sounder as Menvier MWS424SB or similar but approved complete with wiring | Item | 5 |  | 0
16.11 | Allow for programming by THE SPECIALIST SUPPLIER of the Fire Detection and Alarm System | Lump Sump | 1 |  | 0
16.12 | Allow for TRAINING of Client personnel on the fire detection and alarm system operations | Lump Sump | 1 |  | 0
16.13 | Allow for testing and commissioning of the fire detection and alarm system | Lump Sump | 1 |  | 0
| Sub total - 16 |  |  |  | 0
17 | Air-conditions
17.1 | Provide and connection of 18,000BTU split air conditions with all required fitting and fixer | Item | 26 |  | 0
17.2 | Provide and connection of 12,000BTU split air conditions with all required fitting and fixer | Item | 1 |  | 0
| Sub total - 17 |  |  |  | 0
18 | Doors, windows, protection bars and grab rails
18.1 | Provide and fix 215cm height and 180cm width steel of Singapore model design complete with all necessary fittings, fixtures, handles and locks. The rate shall include all fittings, fixtures, painting and varnishing complete. The sample of the door has to be got approved from site engineer. | Item | 1 |  | 0
18.2 | Provide and fix 350cm height and 280cm width steel of Singapore model design complete with all necessary fittings, fixtures, handles and locks. The rate shall include all fittings, fixtures, painting and varnishing complete. The sample of the door has to be got approved from site engineer. | Item | 1 |  | 0
18.3 | For second main gate: Supply and fix 350cm height, 280cm width and with panel of 6cm thick solid core, red hardwood veneer laminated door shutter with hardwood lipping all round; veneer and color to be approved. Complete with; hardwood frame, architrave, transome and all ironmongery including self closure device. The sample of the door has to be got approved from site engineer. | Item | 1 |  | 0
18.4 | For screening and hall: Supply and fix 215cm height, 90cm width and with panel of 6cm thick solid core, red hardwood veneer laminated door shutter with hardwood lipping all round; veneer and color to be approved. Complete with; hardwood frame, architrave, transome and all ironmongery including self closure device. The sample of the door has to be got approved from site engineer. | Item | 6 |  | 0
18.5 | For toilets: Supply and fix 210cm height, 80cm width exported hardwood timber of Singapore model complete with all fitting and fixer. The sample of the door has to be got approved from site engineer. | Item | 4 |  | 0
18.6 | For safe room: Provide and fix 220cm height, 90cm width and with 6.5mm thick ballistic steel panel door framed with UPN-80mm x 40mm x 3mm thick and external door frame of angle iron of 100mm x 100mm x 5mm thick. The door should have very strong hinges made with GI pipes of diameter Ø 40mm and iron bars of diameter Ø 20mm welded nicely to the edge of angle iron of external frame and the UPN. The price will be included fabrication of the door with all required fittings such as lock, hinges, handle etc. as well as three coats of anti-rust paint on internal and external door surfaces including the frame. | Item | 1 |  | 0
18.7 | Provide and fix new double wings PVC framed windows of 150cm width and 120cm height with 6mm thick ordinary glasses and good quality nylon netting including all fittings, fixtures like hinges, handle, lock with very strong fisher and screws for fixing to the walls etc. The sample of the windows must be got approved from site engineer. N.B. Note that the ordinary glasses should be covered by not less than 6µ thick blast resistant films (BRF) with all required fitting and fixer such as adhesive sealing rubber etc. | m² | 16.2 |  | 0
18.8 | Ditto for toilets of 80cm height and 60cm width | m² | 1.92 |  | 0
18.9 | Provide and fix 150cm x 120cm new protection steel flowered decorated model windows bars made by angle iron frame of 20x20x3mm with another frame made by flat iron @ 200mm both ways. Finally provide and fix inside of every square by flowers of flat iron 10mmx2mm with all required fitting, fixer and two coats of antirust paint (See attached detail drawings). | m² | 16.2 |  | 0
18.1 | Ditto for toilets of 80cm height and 60cm width | m² | 1.92 |  | 0
18.11 | Provide and fix at least 100cm height stain less steel handrail made with pipes of external diameter not less than 5cm fixed one side and landing of external steps of the screening room door and standing poles mounting at distance of approximately not less than 65cm c/c. N.B. The grab rail shall be capable of carrying a static load of 150 kg. | m | 3.15 |  | 0
18.12 | Provide and fix one grab rail fixed on each of both the inner and outer surfaces of the cubicle door; which shall not be less than 32 mm and not more than 40 mm in external diameter. The grab rail shall have a grip space of not less than 30 mm clear of each door surface. | Item | 2 |  | 0
18.13 | Provide and fix one folding grab rail on the wide side of the cubicle adjacent to the water-closet (W.C) at a height between 725mm to 750mm above the finished floor level when lowered from the wall. N.B. The folding grab rail shall be capable of carrying a static load of 150 kg. | Item | 1 |  | 0
18.14 | Provide and fix at least two grab rails which shall not be less than 32 mm and not more than 40 mm in external diameter and shall be fixed on the wall leaving a grip space of not less than 30 mm clear of the mounting wall. The two grab rails constructed in one continuous piece is acceptable. The length of grab rail shall not be less than 600 mm. N.B. The grab rail shall be capable of carrying a static load of 150 kg. | Item | 2 |  | 0
| Sub total - 18 |  |  |  | 0
19 | Sanitary system
19.1 | Supply and fix one set of European flash complete ( WC, hand wash, shower with plate etc.) with all required accessory such as mirror, toilet paper holder, towel holder, soap holder etc. | Item | 4 |  | 0
| Sub total - 19 |  |  |  | 0
20 | Connection and manhole construction & misc. items
20.1 | Construction of 1.0mx1.0 masonry cement blocks manholes laid by cement sand mortar of 1:4 with connection PVC pipes of Ø150mm diameter. The item includes all necessary excavation, cement block masonry, cover slab (1:2:4) with nominal reinforcement, plastering and finishing etc. complete as per UNDP engineers satisfaction. | Item | 10 |  | 0
20.2 | Provide and fix all required plumbing material such as height pressure PVC of diameter Ø 1½" feeder pipes from nearest available water source near of the compound, with all required fittings (Elbows, T-joints, regulator valves etc.). The price should include excavation of trench and fixing | Item | 1 |  | 0
| Sub total - 20 |  |  |  | 0
21 | Over roof
21.1 | Construction of medium 6cm (10cm and 2cm to the two edges) thick 1:4 cement sand mortar with adequate slope to the direction of points where is PVC for rain water collections | m³ | 19.7454 |  | 0
21.2 | Provide and cover with tarmac paper for 1m². This activity consists: a. Cleaning the surfaces; b. applying two coats of primer Emulsion (MW) paint; c. Providing of first quality green colored tarmac paper with fine aggregate on top; d. burning of tarmac paper by special equipment designed to burn. | m² | 329.0895 |  | 0
21.3 | Provide and fix PVC of diameter Ø 11cm to 4 points where is recommended the site Engineer probably attached to reinforced concrete columns for surrounding walls of the building | Item | 8 |  | 0
21.4 | Construction of masonry cement blocks of 90cm height top crown parapet wall. The wall should be made with cement blocks wall of 0.40mx0.20mx0.20m laid and jointed by cement sand mortar of 1:6 mixing ratio | m² | 68.904 |  | 0
21.5 | Construction of 10cm thick and 20cm wide RC copping beam on top of crown parapet wall. The beam should be 1:2:4 mixing ratio with # 4 Y10 and staffs of 6mm@ 250mm/cc | m² | 1.5312 |  | 0
21.6 | Construction of masonry cement blocks wall of 90cm height 40cm x 40cm wide to cover the iron bars on top of slab roof. The wall should be made with cement blocks wall of 0.40mx0.20mx0.20m laid and jointed by cement sand mortar of 1:6 mixing ratio. Note that the price should be included supplying of fixing to the iron bars by 6 pieces PVC pipes of diameter 3cm and 10cm height. | Item | 21 |  | 0
21.7 | Apply on 20mm thick internal external plastering of cement sand mortar of 1:5 mixing ratio for all new constructed surfaces crown parapet walls. | m² | 168.432 |  | 0
21.8 | Apply two coats white wash with white emulsion filler on all wall surfaces, and filling with it on all depressed area of the wall surfaces including the protection iron bars of columns over the slab roof. | m² | 198.672 |  | 0
21.9 | Apply two coats of light yellow distemper inside and outside of building wall surfaces including the protection iron bars of columns over the slab roof and with white light grey on external edges of copping beam. | m² | 198.672 |  | 0
| Sub total - 21 |  |  |  | 0
| Total for Data collection block of new NIEC building near of MIA |  |  |  | 0

## 1 open space safe & server
S.n. | Description | Unit | QTY | Rate in $ | Amount in $
E. | Construction of one open space server room and safe haven
22 | Substructure works
Excavation and Earthwork (Provisional)
20.1 | Excavation of soft soil for foundation trenches of 60cm wide and 130cm depth starting from stripped level. When construction of foundation finishes, these materials should be returning and filled around foundation, where extra surplus materials must be dumped at least 2km away from the site as per directed by UNDP engineers. | m³ | 83.8344 |  | 0
20.2 | Ditto for foundation wall at the staircase side of 60cm wide and 221cm depth. | m³ | 14.8512 |  | 0
20.3 | Ditto for 20 columns footings of 120cmx120cmx175cm depth. | m³ | 50.4 |  | 0
20.4 | Ditto for 4 columns footings of 120cmx120cmx266cm depth. | m³ | 15.3216 |  | 0
| Selected filling |  |  |  | 0
21.1 | Provide and compact 34cm height first layer with approved marram or other approved backfilling materials over the existing floor of whole building including the toilets inside the safe haven and server room of the building. | m³ | 81.7061 |  | 0
21.2 | Provide and compact 30cm height hardcore layer with approved materials over the existing floor of whole building including the toilets of safe haven and server room of the building | m³ | 72.0936 |  | 0
| Anti-termite treatment |  |  |  | 0
21.3 | Provide and apply on the upper surfaces of hardcore layer a chemical spry or powder anti-termite treatment as "Premise 200 SC" or other equal and approved anti insecticide materials. | m² | 240.312 |  | 0
| Damp proof membrane |  |  |  | 0
21.4 | Provide and lay 1000-gauge polythene or other equal and approved damp proof membrane laid under surface bed with 300mm side and end laps (measured net- allow for laps) | m² | 240.312 |  | 0
| Concrete work in substructure |  |  |  | 0
20.5 | Construction of 5cm thick and 60cm wide Plain cement concrete of class 15 ( 1:3:6 mixing) under the foundation walls of the building. | m³ | 3.5604 |  | 0
20.6 | Ditto for internal subdivision wall of the toilets of safe haven and server room of 40cm wide and 5cm thick. | m³ | 0.14 |  | 0
20.7 | Ditto for 24 columns footing of 120cmx120cmx5cm depth. | m³ | 1.728 |  | 0
| Foundation Walling |  |  |  | 0
20.8 | Construction of 40cm wide and 179cm height (125cm under ground and 54cm above ground) foundation wall made by rubble stone jointed and connected by cement sand mortar of mixing ratio 1:6 | m³ | 99.2949 |  | 0
20.9 | Ditto for foundation wall at the staircase side of 40cm wide and 211cm depth. | m³ | 11.4784 |  | 0
20.1 | Ditto for internal subdivision wall of the toilets of safe haven and server rooms of 40cm wide and 54cm height. | m³ | 1.512 |  | 0
| Sub total - 22 |  |  |  | 0
23 | Super structure works
Plain and reinforced concrete works
23.1 | Construct 120cmx120cmx40cm reinforced concrete of 1:2:4 mixing ratio for footing of the columns with 9 numbers of Y16 both ways. | m³ | 13.824 |  | 0
23.2 | Ditto for 20 columns neck of 40cm x40cm and 204cm height with 10 numbers of Y 16mm | m³ | 6.528 |  | 0
23.3 | Ditto for 4 columns neck of 40cm x40cm and 236cm height with 10 numbers of Y 16mm | m³ | 1.5104 |  | 0
23.4 | Construct 40cm wide, 20cm thick of reinforced concrete beam of 1:2:4 mixing ratio with # 8 Y16 and staffs of 8mm@ 250mm/cc over foundation wall including the toilets | m³ | 12.7424 |  | 0
23.5 | Laying 7cm thick plain cement concrete of 1:3:6 mixing ratio over newly constructed hardcore layer with proper finish. | m³ | 16.8218 |  | 0
23.6 | Construction of 1:2:4 reinforced concrete wall of 20cm thick for the safe-haven (Banker). The wall must be reinforced with two line of nets made by iron bars of diameter Ø 12 for main at horizontal direction and vertical for 10mm reinforcement bars @ 15cm c/c both ways. Note that wall should be protected from the sun and kept moist for at least 10 days. | m³ | 127.472 |  | 0
23.7 | Construct 24 pieces of 30cm x 40cm reinforced concrete columns of 315cm height of the building. The concrete must be 1:2:4 mixing ratio and reinforced with No. 8 Y16 and staffs of Ø 8mm @250mm c/c. N.B. Note that the columns should be protected from sun and kept moist for at least 10 days. | m³ | 9.072 |  | 0
23.8 | Construct 20cm wide, 15cm thick of reinforced concrete 2.2m level beam of 1:2:4 mixing ratio with # 6 Y14 and staffs of 6mm@ 250mm/cc. This is for all constructed walls including toilet of safe haven and server rooms. | m³ | 3.8964 |  | 0
23.9 | Construction of reinforced concrete corbel on external top edges of windows. The corbel must be constructed in three steps of 5cm height each with the top layer of 250cmx 70cm, where the second layer is 240cm x 65cm and the last layer at the bottom is 226cmx60cm, with two supporting braces (see detail drawings). The concrete should be mixed by 1:2:4 and reinforced with iron bars of diameter Ø12mm and Ø 10mm | m³ | 1.4772 |  | 0
23.1 | Construct of 180 cm x 30 cm x 5cm reinforced concrete window sills at bottom edge windows for offices and toilets. The concrete should be mixed by 1:2:4 with # 3 Y12 and staffs of 8 mm @ 200mm/cc | m³ | 0.162 |  | 0
23.11 | Construction of reinforced concrete 1:2:4 mixing ratio loaded beam of 30cm width and 65cm height (15cm inside of the slab and 50cm outside). The concrete should be reinforced with 6 pieces of straight bars diameter ∅ 16mm (2 on top and 4 at the bottom), 2 pieces of bended bars diameter ∅ 16mm and 2 reinforcement bars of diameter ∅ 16mm of 300cm length on top of the columns. All these bars should be united by staffs of 8mm@ 250mm/cc. N.B. Note that the calculated quantities volume is only the lowest part of the beams (50cmx30cm) as the top part is inside of the slab and will considered part of the slab structure. | m³ | 13.68 |  | 0
23.12 | Construction of reinforced concrete 1:2:4 mixing ratio final beam (Not loaded) of 20cm width and 35cm height (15cm inside of the slab and 20cm outside). The concrete should be reinforced with 6 pieces of bars diameter ∅ 16mm with staffs of iron bars of 8mm@ 250mm/cc | m³ | 3.2112 |  | 0
| Sub total - 23 |  |  |  | 0
24 | Construction of steps access
24.1 | Construction of internal external steps of 30cm trade and 15cm rise made by rubble stone jointed and connected with cement sand mortar of 1:6, with 10cm plain cement concrete of 1:2:4 on top of stone base | Item | 4 |  | 0
| Sub total - 24 |  |  |  | 0
25 | Construction of concrete blocks
25.1 | Construction 280cm height walls of masonry cement blocks (0.40mx0.20mx0.20m) wall laid and jointed by cement sand mortar of 1:6 mixing ratio. Note that price will be include reinforcement hoop iron made by fixing of two lines of iron bars of diameter Ø 8mm for every alternate course. N.B. Note that the given height is only the cement blocks wall which is not included the ring beams | m² | 164.572 |  | 0
25.2 | Ditto for the subdivision wall of toilets of the two safe haven and server room walls of 285cm height. N.B. Note that the given height is only the cement blocks wall which is not included the ring beams | m² | 17.73 |  | 0
| Sub total - 25 |  |  |  | 0
26 | R.C roofing
26.1 | R.C (1:2:4 Mixing ratio) slab cover of 15cm thick with Ø 12mm main bars and 10mm distribution bars both ways at top and bottom and distanced 15cm c/c .Formwork must be accurately set out, this means when remove the formwork all surfaces should be smooth and NO NEED TO BE PLASTERED, so that the resulting concrete product is in a right place and is of correct shape and size. N.B. The structure should be kept moist and protect from the sun for at least 10 days. | m³ | 49.1215 |  | 0
26.2 | Construction of 12 numbers of trapezoid shape reinforced concrete braces under the projection of the slab of 25cm thick with top width of 73cm and bottom width of 40cm and 30cm height reinforced with iron bars of diameter Ø16 and staffs of diameter 8mm. | m³ | 0.5085 |  | 0
| Sub total - 26 |  |  |  | 0
27 | Flooring
27.1 | Construction of 60cm x 60cm non slippery ceramic floor tiles for all pavement of the building laid and jointed with cement sand mortar of 1:2 mixing. Note that the price is included the floor hall, toilets, safe haven and server room | m² | 277.674 |  | 0
27.2 | Construction of 60cm x 10cm ceramic skirting tiles for all bottom edge of the walls of the building laid and jointed with cement sand mortar of 1:2 mixing. Note that the price is included the skirting of safe haven, server room and the corridor. | m | 161.42 |  | 0
27.3 | Construction of 60cm x 60cm non slippery local made terrazzo floor on the top surfaces of two step access outside of the building. The terrazzo should be divided by PVC or steel boundary edges with light green color. Note that the proportion of cement sand must be 1:2 mixing. | Item | 1 |  | 0
27.4 | Construction of ceramic floor marble tiles on the trade and rise of the two steps inside of the building corridor. The marble must be laid and jointed with cement sand mortar of 1:2 mixing. The sample of the marble has to be got approved from site engineer before fixing. N.B. Note that the given area is only the trades of staircase of 30cmx120cm, but the bidder should include his/her prices the budget of the rises of 15cmx120cm | m² | 4.5 |  | 0
27.5 | Construction of 140cm width along external edges of the building with floor paving made by cement sand interlocking with all required fitting and fixer such as retaining wall of cement blocks to external edges, aggregate powder to lay the floor before fixing the paving etc. Also the price should be added construction of retaining wall made by cement blocks laid and jointed with cement sand mortar of 1:6 mixing with adequate foundation wall of at least 40cm under ground. | m² | 56.196 |  | 0
| Sub total - 27 |  |  |  | 0
28 | Plastering and other decoration works
28.1 | Apply of first coat on 30mm thick plastering of cement sand mortar of 1:6 mixing ratio for all external new constructed stone wall surfaces | m² | 24.084 |  | 0
28.2 | Apply 20mm thick on internal external plastering with cement sand mortar of 1:5 mixing ratio for all new constructed wall surfaces including stone walls. | m² | 686.4986 |  | 0
28.3 | Apply on 10mm thick rough cast plastering of cement sand mortar of 1:2 mixing ratio on external 1,200mm bottom part of the windows sills of wall surfaces including the first floor. Note that the wall should be market by blocks of 52cmx26cm with lines approximately 1cm wide. | m² | 48.168 |  | 0
28.4 | Construction of 270cm height ceramic wall tiles for all walls of the toilets laid and jointed with cement sand mortar of 1:2 mixing | m² | 34.44 |  | 0
28.5 | Apply two coats white wash with white emulsion filler on all wall surfaces, and filling with it on all depressed area of the wall surfaces including the under ceiling with external projection of under ceiling of the slab. | m² | 931.365 |  | 0
28.6 | Apply two coats of light yellow distemper inside and outside of building walls and white distemper on under ceiling | m² | 931.365 |  | 0
28.7 | Apply two coats of light grey distemper paint on the rough casted surfaces at external walls of building. | m² | 48.168 |  | 0
| Sub total - 28 |  |  |  | 0
29 | Electricity
INTERIOR ELECTRICAL SERVICES
Lighting
29.1 | Type F1: 1200mm 1x18w Surface Mounted LED light fitting with CAT 2 Louvered with maximum unified glare of 19 and with LED lamp as "Thomson" LED (1x1750LM MIN)The lamp shall have a minimum of 30,000 hours lifetime; and with 50000 times switching cycles. The color temperature shall be 3000 - 7000K and luminous flux of 1500 - 1700 lumens. | Item | 40 |  | 0
29.2 | Type F1E: Ditto as Type F1 above but emergency version of 3hour duration | Item | 20 |  | 0
29.3 | Type E- 21w IP44 die-cast aluminum light fitting with clear diffuser and complete with lamp as massive Sussex CAT 81657/01/30 | Item | 4 |  | 0
29.4 | Type 4 - 8.5w IP54 LED spherical ball light fitting complete with LED lamps for toilets | Item | 2 |  | 0
29.5 | Type EXIT: 8W, Non-maintained illuminated emergency exit light sign luminaire with white steel body. Emergency lighting of 3 hour duration | Item | 2 |  | 0
| Sub total - 29 |  |  |  | 0
30 | Light Switches
30.1 | Supply, install and connect following 10A lighting switches on recessed switchboxes wired in 1.5 sq.mm PVC single core copper cables enclosed in concealed HG PVC conduits complete with all necessary accessories:
30.2 | 1 gang 1 way | Item | 8 |  | 0
30.3 | 1 gang 2 ways | Item | 3 |  | 0
30.4 | 2 gangs 2 ways | Item | 2 |  | 0
30.5 | 3 gangs 1 way | Item | 1 |  | 0
30.6 | Intermediate switch | Item | 1 |  | 0
| Sub total - 30 |  |  |  | 0
31 | Power sockets, Isolators and DP Switches
31.1 | Supply, install, test and commission the following power sockets as shown on drawing, as per the preamble, the specifications and supervision engineer's requirements.
31.2 | Supply, install and connect 13Amp standard twin socket outlets for normal power as MK or equal and approved (5numbers for each room of 6.2mx3.68m). Note that the sockets must be fixed at least 60cm from the pavement level. | Item | 42 |  | 0
31.3 | Supply, install and connect 13Amp standard twin socket outlets for normal power as MK or equal and approved for the Wi-Fi at the corridor of the building. Note that the sockets must be fixed at least 60cm from the bottom level of concrete slab. | Item | 6 |  | 0
31.4 | Supply, install and connect 15A un-switched DP outlet plate with fuse connector and neon indicator for Fire Alarm Panel power supply and marked "FACP" | Item | 2 |  | 0
31.5 | Supply, install and connect 30A switched TPN industrial isolator outlet plate with connector Split Air Conditioning Units power supply and marked "AIR CONDITIONER" respectively | Item | 10 |  | 0
| Sub total - 31 |  |  |  | 0
32 | Cables, Cable pathways and Conduits
32.1 | Supply, install, test and commission 450/750 volts 6491X cables with all required accessories for proper installation and operation including conduits, pipes( each cable in separate conduit or pipe), cable lugs, ties... etc. as shown on drawing, as per the preamble, the specifications and supervision engineer's requirements.
32.2 | Supply, install and connect complete 3x1.5 sq. mm color-coded SC cables to lighting points drawn in Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 64 |  | 0
32.3 | Supply, install and connect complete 3x2.5 sq. mm color-coded SC cables to lighting points drawn in Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 4 |  | 0
32.4 | Supply, install and connect complete 3x2.5 sq. mm color-coded SC cables to socket power points drawn in ring and within Concealed /surface 25mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 42 |  | 0
32.5 | Supply, install and connect complete 3x2.5 sq. mm color-coded SC cables to Fire Alarm Panel power points drawn in spur and within Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 2 |  | 0
32.6 | Supply, install and connect complete 3x2.5 sq. mm color-coded SC cables for Split Air Conditioning Units power supply drawn in spur and within Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 10 |  | 0
32.7 | Supply and install 4C, 50sq.mm XLPE/SWA /PVC Copper Cable from generator at West side of main entrance gate DB to new building DB' complete with cable lugs and cable glands | m | 200 |  | 0
32.8 | Excavate trench for XLPE/SWA /PVC Copper Cable not exceeding 300 mm and average 500 mm deep, part return, fill in, ram the ground (Final ground finish with direction of site engineer) | m | 170 |  | 0
32.9 | Electrical ducts and manholes |  |  |  | 0
32.1 | Supply and install the following uPVC ducts at 600mm below ground level. Rate to be inclusive of trenching at 600mm below ground level, back filling of trenches, and laying of "DANGER" cable tiling, reinstatement and making of good of ground as per directed by the site engineer: |  |  |  | 0
32.11 | a) 2x100mm uPVC duct | m | 170 |  | 0
32.12 | Construct 600mm x 600mm x 600mm deep [internal dimensions] reinforced concrete power manhole complete with heavy duty cast iron cover | Item | 8 |  | 0
| Sub total - 32 |  |  |  | 0
33 | Distribution Boards
33.1 | Supply, install, connect, testing and commission the following final distribution boards, distribution terminal blocks according to drawings, specifications and relevant codes and as Merlin Gerin or equal and approved
33.2 | Supply, install, connect-up complete 250 Amp 4 way TP/N main Distribution Board as Merlin Gerin or equal and approved for normal power supply, for main DB (UNSOM main switch board at back side of the building) complete with integral isolator, and 3.No 63 Amps MCCBs as specified | Item | 1 |  | 0
33.3 | Supply, install, connect-up complete 100 Amp 6way TP/N MCB Distribution Board as Merlin Gerin or equal and approved for normal power supply, for ground floor complete with integral isolator as specified | Item | 1 |  | 0
33.4 | Supply, install, and connect 100Amp, 4 way SP/N Consumer unit , as Merlin Gerin or approved equivalent, as shown on schematic wiring drawing for lightings load only | Item | 1 |  | 0
33.5 | Supply, install, test and commission miniature circuit breakers (MCBs) rated at 500Vac for above items with 10KA short circuit current according to schematics, specifications and relevant codes and as Merlin Gerin or equal and approved |  |  |  | 0
33.6 | 10A (TP)- 30mA | Item | 1 |  | 0
33.7 | 30A (TP)- 30mA | Item | 12 |  | 0
33.8 | 10A (SPN)- 30mA | Item | 1 |  | 0
33.9 | Blanking plates for items above(TP) | Item | 1 |  | 0
33.1 | Blanking plates for items above(SP) | Item | 1 |  | 0
| Sub total - 33 |  |  |  | 0
34 | Earthling
34.1 | Supply, install, test and commission Copper earthling mat for electrical system of 1200mmx1200mm dimensions constructed of 25mm x 3mm copper tape laid 1000mm deep in ground and complete with 10sq.mm earth lead cable for earthling in Masonry earth pit and with concrete removable cover marked "EARTH" | Lump Sump | 1 |  | 0
34.2 | Allow for testing and commissioning Electrical Installations | Lump Sump | 1 |  | 0
34.3 | FIRE DETECTION AND ALARM SYSTEM |  |  |  | 0
34.4 | Supply and install 1.5mm sq. fire rated copper cable for Smoke detector outlet as per layouts | Item | 12 |  | 0
34.5 | Supply and install 1.5mm sq. fire rated copper cable for Sounder outlet per layouts | Item | 3 |  | 0
34.6 | Supply and install 1.5mm sq. fire rated copper cable for Call point fire break glass unit outlet per layouts | Item | 4 |  | 0
34.7 | Supply and install complete 4-zone conventional fire alarm panel as Menvier MF9304 or equivalent by HF Fire but approved by engineer as per the specifications | Item | 1 |  | 0
34.8 | Supply and install conventional surface mounted Call point fire break glass unit as menvier MBG914 or similar but approved complete with conduit and wiring as shown on the drawings | Item | 4 |  | 0
34.9 | Supply and install conventional optical Smoke Detector / Sensors unit as Menvier MID810 or similar but approved complete with conduit and wiring a shown on the drawings | Item | 12 |  | 0
34.1 | Supply and install 93 mm diameter conventional electronic sounder as Menvier MWS424SB or similar but approved complete with wiring | Item | 3 |  | 0
34.11 | Allow for programming by THE SPECIALIST SUPPLIER of the Fire Detection and Alarm System | Lump Sump. | 1 |  | 0
34.12 | Allow for TRAINING of Client personnel on the fire detection and alarm system operations | Lump Sump. | 1 |  | 0
34.13 | Allow for testing and commissioning of the fire detection and alarm system | Lump Sump. | 1 |  | 0
| Sub total - 34 |  |  |  | 0
35 | Air-conditions
35.1 | Provide and connection of 18,000BTU split air conditions with all required fitting and fixer | Item | 12 |  | 0
| Sub total - 35 |  |  |  | 0
36 | Doors, windows, protection bars and grab rails
36.1 | For server room and hall: Supply and fix 215cm height, 90cm width and with panel of 6cm thick solid core, red hardwood veneer laminated door shutter with hardwood lipping all round; veneer and color to be approved. Complete with; hardwood frame, architrave, transome and all ironmongery including self closure device. The sample of the door has to be got approved from site engineer. | Item | 4 |  | 0
36.2 | For toilets: Supply and fix 210cm height, 80cm width exported hardwood timber of Singapore model complete with all fitting and fixer. The sample of the door has to be got approved from site engineer. | Item | 2 |  | 0
36.3 | For safe room: Provide and fix 220cm height, 90cm width and with 6.5mm thick ballistic steel panel door framed with UPN-80mm x 40mm x 3mm thick and external door frame of angle iron of 100mm x 100mm x 5mm thick. The door should have very strong hinges made with GI pipes of diameter Ø 40mm and iron bars of diameter Ø 20mm welded nicely to the edge of angle iron of external frame and the UPN. The price will be included fabrication of the door with all required fittings such as lock, hinges, handle etc. as well as three coats of anti-rust paint on internal and external door surfaces including the frame. | Item | 2 |  | 0
36.4 | Provide and fix new double wings PVC framed windows of 150cm width and 120cm height with 6mm thick ordinary glasses and good quality nylon netting including all fittings, fixtures like hinges, handle, lock with very strong fisher and screws for fixing to the walls etc. The sample of the windows must be got approved from site engineer. N.B. Note that the ordinary glasses should be covered by not less than 6µ thick blast resistant films (BRF) with all required fitting and fixer such as adhesive sealing rubber etc. | m² | 10.8 |  | 0
36.5 | Provide and fix 150cm x 120cm new protection steel flowered decorated model windows bars made by angle iron frame of 20x20x3mm with another frame made by flat iron @ 200mm both ways. Finally provide and fix inside of every square by flowers of flat iron 10mmx2mm with all required fitting, fixer and two coats of antirust paint (See attached detail drawings). | m² | 10.8 |  | 0
36.6 | Provide and fix one grab rail fixed on each of both the inner and outer surfaces of the cubicle door; which shall not be less than 32 mm and not more than 40 mm in external diameter. The grab rail shall have a grip space of not less than 30 mm clear of each door surface. | Item | 4 |  | 0
36.7 | Provide and fix one folding grab rail on the wide side of the cubicle adjacent to the water-closet (W.C) at a height between 725mm to 750mm above the finished floor level when lowered from the wall. N.B. The folding grab rail shall be capable of carrying a static load of 150 kg. | Item | 2 |  | 0
36.8 | Provide and fix at least two grab rails which shall not be less than 32 mm and not more than 40 mm in external diameter and shall be fixed on the wall leaving a grip space of not less than 30 mm clear of the mounting wall. The two grab rails constructed in one continuous piece is acceptable. The length of grab rail shall not be less than 600 mm. N.B. The grab rail shall be capable of carrying a static load of 150 kg. | Item | 4 |  | 0
| Sub total - 36 |  |  |  | 0
37 | Sanitary system
37.1 | Supply and fix one set of European flash complete ( WC, hand wash, shower with plate etc.) with all required accessory such as mirror, toilet paper holder, towel holder, soap holder etc. | Item | 2 |  | 0
| Sub total - 37 |  |  |  | 0
38 | Connection and manhole construction & misc. items
38.1 | Construction of 1.0mx1.0 masonry cement blocks manholes laid by cement sand mortar of 1:4 with connection PVC pipes of Ø150mm diameter. The item includes all necessary excavation, cement block masonry, cover slab (1:2:4) with nominal reinforcement, plastering and finishing etc. complete as per UNDP engineers satisfaction. | Item | 10 |  | 0
38.2 | Provide and fix all required plumbing material such as height pressure PVC of diameter Ø 1½" feeder pipes from nearest available water source near of the compound, with all required fittings (Elbows, T-joints, regulator valves etc.). The price should include excavation of trench and fixing | Item | 1 |  | 0
| Sub total - 38 |  |  |  | 0
39 | Over roof
39.1 | Construction of medium 6cm (10cm and 2cm to the two edges) thick 1:4 cement sand mortar with adequate slope to the direction of points where is PVC for rain water collections | m³ | 19.6486 |  | 0
39.2 | Provide and cover with tarmac paper for 1m². This activity consists: a. Cleaning the surfaces; b. applying two coats of primer Emulsion (MW) paint; c. Providing of first quality green colored tarmac paper with fine aggregate on top; d. burning of tarmac paper by special equipment designed to burn. | m² | 327.4764 |  | 0
39.3 | Provide and fix PVC of diameter Ø 11cm to 4 points where is recommended the site Engineer probably attached to reinforced concrete columns for surrounding walls of the building | Item | 6 |  | 0
39.4 | Construction of masonry cement blocks of 90cm height top crown parapet wall. The wall should be made with cement blocks wall of 0.40mx0.20mx0.20m laid and jointed by cement sand mortar of 1:6 mixing ratio | m² | 65.52 |  | 0
39.5 | Construction of 10cm thick and 20cm wide RC copping beam on top of crown parapet wall. The beam should be 1:2:4 mixing ratio with # 4 Y10 and staffs of 6mm@ 250mm/cc | m² | 1.456 |  | 0
39.6 | Construction of masonry cement blocks wall of 90cm height 40cm x 40cm wide to cover the iron bars on top of slab roof. The wall should be made with cement blocks wall of 0.40mx0.20mx0.20m laid and jointed by cement sand mortar of 1:6 mixing ratio. Note that the price should be included supplying of fixing to the iron bars by 6 pieces PVC pipes of diameter 3cm and 10cm height. | Item | 24 |  | 0
39.7 | Apply on 20mm thick internal external plastering of cement sand mortar of 1:5 mixing ratio for all new constructed surfaces crown parapet walls. | m² | 160.16 |  | 0
39.8 | Apply two coats white wash with white emulsion filler on all wall surfaces, and filling with it on all depressed area of the wall surfaces including the protection iron bars of columns over the slab roof. | m² | 194.72 |  | 0
39.9 | Apply two coats of light yellow distemper inside and outside of building wall surfaces including the protection iron bars of columns over the slab roof and with white light grey on external edges of copping beam. | m² | 194.72 |  | 0
| Sub total - 39 |  |  |  | 0
| Total for one open space server room and safe haven of new NIEC building near of MIA |  |  |  | 0

## Staircase access
S.n. | Description | Unit | QTY | Rate in $ | Amount in $
F. | Construction of staircase access of the building
40 | Substructure works
Excavation and Earthwork (Provisional)
40.1 | Excavation of soft soil for foundation trenches of 60cm wide and 129cm depth starting from stripped level. When construction of foundation finishes, these materials should be returning and filled around foundation, where extra surplus materials must be dumped at least 2km away from the site as per directed by UNDP engineers. | m³ | 22.0745 |  | 0
40.2 | Ditto for 8 columns footings of 120cmx120cmx174cm depth. | m³ | 20.0448 |  | 0
| Selected filling |  |  |  | 0
40.3 | Provide and compact 37cm height first layer with approved marram or other approved backfilling materials over the existing floor of whole building including the toilets inside the safe haven and server room of the building. | m³ | 16.7566 |  | 0
40.4 | Provide and compact 30cm height hardcore layer with approved materials over the existing floor of whole building including the toilets of safe haven and server room of the building | m³ | 13.5864 |  | 0
| Anti-termite treatment |  |  |  | 0
40.5 | Provide and apply on the upper surfaces of hardcore layer a chemical spry or powder anti-termite treatment as "Premise 200 SC" or other equal and approved anti insecticide materials. | m² | 45.288 |  | 0
| Damp proof membrane |  |  |  | 0
40.6 | Provide and lay 1000-gauge polythene or other equal and approved damp proof membrane laid under surface bed with 300mm side and end laps (measured net- allow for laps) | m² | 45.288 |  | 0
| Concrete work in substructure |  |  |  | 0
40.7 | Construction of 5cm thick and 60cm wide Plain cement concrete of class 15 ( 1:3:6 mixing) under the foundation walls of the building. | m³ | 0.8556 |  | 0
40.8 | Ditto for 8 columns footing of 120cmx120cmx5cm depth. | m³ | 0.576 |  | 0
| Foundation Walling |  |  |  | 0
40.9 | Construction of 40cm wide and 181cm height (124cm under ground and 57cm above ground) foundation wall made by rubble stone jointed and connected by cement sand mortar of mixing ratio 1:6 | m³ | 19.4177 |  | 0
| Sub total - 40 |  |  |  | 0
41 | Super structure works
Plain and reinforced concrete works
41.1 | Construct 120cmx120cmx40cm reinforced concrete of 1:2:4 mixing ratio for footing of the columns with 9 numbers of Y16 both ways. | m³ | 4.608 |  | 0
41.2 | Ditto for 8 columns neck of 40cm x40cm and 186cm height with 10 numbers of Y 16mm | m³ | 2.3808 |  | 0
41.3 | Construct 40cm wide, 20cm thick of reinforced concrete beam of 1:2:4 mixing ratio with # 8 Y16 and staffs of 8mm@ 250mm/cc over foundation wall including the toilets | m³ | 3.4976 |  | 0
41.4 | Laying 7cm thick plain cement concrete of 1:3:6 mixing ratio over newly constructed hardcore layer with proper finish. | m³ | 3.1702 |  | 0
41.5 | Construct 8 pieces of 30cm x 40cm reinforced concrete columns of 345cm height of the building. The concrete must be 1:2:4 mixing ratio and reinforced with No. 8 Y16 and staffs of Ø 8mm @250mm c/c. N.B. Note that the columns should be protected from sun and kept moist for at least 10 days. | m³ | 3.312 |  | 0
41.6 | Construct 20cm wide, 15cm thick of reinforced concrete 2.2m level beam of 1:2:4 mixing ratio with # 6 Y14 and staffs of 6mm@ 250mm/cc. This is for all constructed walls including toilet of safe haven and server rooms. | m³ | 1.3116 |  | 0
41.7 | Construct of 330 cm x 30 cm x 5cm reinforced concrete window sills at bottom edge window of the staircase. The concrete should be mixed by 1:2:4 with # 3 Y12 and staffs of 8 mm @ 200mm/cc | m³ | 0.04995 |  | 0
41.8 | Construction of reinforced concrete 1:2:4 mixing ratio loaded beam of 30cm width and 65cm height (15cm inside of the slab and 50cm outside). The concrete should be reinforced with 6 pieces of straight bars diameter ∅ 16mm (2 on top and 4 at the bottom), 2 pieces of bended bars diameter ∅ 16mm and 2 reinforcement bars of diameter ∅ 16mm of 300cm length on top of the columns. All these bars should be united by staffs of 8mm@ 250mm/cc. N.B. Note that the calculated quantities volume is only the lowest part of the beams (50cmx30cm) as the top part is inside of the slab and will considered part of the slab structure. | m³ | 4.77 |  | 0
41.9 | Construction of reinforced concrete 1:2:4 mixing ratio final beam (Not loaded) of 20cm width and 35cm height (15cm inside of the slab and 20cm outside). The concrete should be reinforced with 6 pieces of bars diameter ∅ 16mm with staffs of iron bars of 8mm@ 250mm/cc | m³ | 0.5328 |  | 0
| Sub total - 41 |  |  |  | 0
42 | Construction of internal steps access inside of the building
42.1 | Construction of internal external step of 30cm trade and 15cm rise made by rubble stone jointed and connected with cement sand mortar of 1:6, with 10cm plain cement concrete of 1:2:4 on top of stone base
42.2 | Construction of 30cm legth, 15cm thick and 200cm lengrth of plain cement conrete of 1:2:4 mixing ratio over the existing ring beam | m³ | 0.09 |  | 0
42.3 | Constrution of exported marle on the steps and rise of the staitcase | m² | 0.9 |  | 0
42.4 | For the front access steps in the middle of the two ramps: Construction of 206cm wide and 700cm length made by stone laid and jointed with cement sand mortar of 1:6 mixing. After it pour on top with 10cm thick plain cement concrete of 1:2:4 mixing ratio. Note that this steps should be kept moist and protect from the sun for at least 10 days. See the detail drawings for the rise and trades dimensions |  |  |  | 0
42.5 | External acces steps in the middle: |  |  |  | 0
42.6 | For the front access steps in the middle of the ramp: Construction of 80cm wide and 940cm length made stone laid and jointed with cement sand mortar of 1:6 mixing. After it poured on top by 10cm thick plain cement concrete of 1:2:4 mixing ratio. Note that this ramp should be kept moist and protect from the sun for at least 10 days. |  |  |  | 0
42.7 | Excavation of soft soil for foundation trenches of the two wing walls of 940cm legth, 60cm wide and 60cm depth starting from stripped level. When construction of foundation finishes, these materials should be returning and filled around foundation, where extra surplus materials must be du | m³ | 6.768 |  | 0
42.8 | Construction of 5cm thick and 60cm wide PCC of 1:3:6 mixing ratio over the two foundation walls. | m³ | 0.564 |  | 0
42.9 | Construction of 40cm wide and 55 cm height foundation walling over the PCC | m³ | 4.136 |  | 0
42.1 | Construction of multi-trapezoide shape of masonry cement blocks (0.40mx0.20mx0.20m) wall laid and jointed by cement sand mortar of 1:6 mixing ratio. Note that price will be include reinforcement hoop iron made by fixing of two lines of iron bars of diameter Ø 8mm for every alternate course. N.B. Note that the given height is only the cement blocks wall which is not included the ring beams | m² | 10.6175 |  | 0
42.11 | Backfilling materials with marram or other approved materials. | m³ | 4.247 |  | 0
42.12 | Construction of 940cm legth, 80cm wide and 15cm height stone basement made with ruble stone jointed and connected with cement sand mortar of 1:6 ratio. | m³ | 1.128 |  | 0
42.13 | Construction of 10cm thick of plain cement conrete of 1:2:4 mixing ratio over the trade and rise of steps and landing area | m³ | 0.6648 |  | 0
42.14 | For the two access ramps at the front |  |  |  | 0
42.15 | For the two front access ramp: Construction of 164cm wide and 940cm length made stone laid and jointed with cement sand mortar of 1:6 mixing. After it poured on top by 10cm thick plain cement concrete of 1:2:4 mixing ratio. Note that this ramp should be kept moist and protect from the sun for at least 10 days. |  |  |  | 0
42.16 | Excavation of soft soil for foundation trenches of the two retaining walls of 1200cm legth, 60cm wide and 60cm depth each starting from stripped level. When construction of foundation finishes, these materials should be returning and filled around foundation, where extra surplus materials must be du | m³ | 6.768 |  | 0
42.17 | Construction of 5cm thick and 60cm wide PCC of 1:3:6 mixing ratio over the two foundation walls. | m³ | 0.564 |  | 0
42.18 | Construction of multi-trapezoide shape of masonry cement blocks (0.40mx0.20mx0.20m) wall of to width is 225cm while the bottom width is 60cm laid and jointed by cement sand mortar of 1:6 mixing ratio. Note that price will be include reinforcement hoop iron made by fixing of two lines of iron bars of diameter Ø 8mm for every alternate course. N.B. Note that the given height is only the cement blocks wall which is not included the ring beams | m² | 26.79 |  | 0
42.19 | 30cm wide and 10cm height reinforced concrete copping beam on top of the retaining wall. The concrete must be reinforced with 4 number of iron mars of diameter Y 10 and staffed with iron bars of diameter y 8 @ 250cm c/c. | m³ | 0.564 |  | 0
42.2 | Backfilling materials with marram or other approved materials. | m³ | 19.1585 |  | 0
42.21 | Provide and compacting of hardcore layer of 779cm length, 164cm wide and 30cm height. | m³ | 7.6654 |  | 0
42.22 | Construction of 10cm thick of plain cement concrete of 1:2:4 mixing ratio over the trade and rise of steps and landing area | m³ | 2.5551 |  | 0
| Sub total - 42 |  |  |  | 0
43 | Construction of concrete blocks
43.1 | Construction 310cm height walls of masonry cement blocks (0.40mx0.20mx0.20m) wall laid and jointed by cement sand mortar of 1:6 mixing ratio. Note that price will be include reinforcement hoop iron made by fixing of two lines of iron bars of diameter Ø 8mm for every alternate course. N.B. Note that the given height is only the cement blocks wall which is not included the ring beams | m² | 98.6723 |  | 0
| Sub total - 43 |  |  |  | 0
44 | R.C roofing
44.1 | R.C (1:2:4 Mixing ratio) slab cover of 15cm thick with Ø 12mm main bars and 10mm distribution bars both ways at top and bottom and distanced 15cm c/c .Formwork must be accurately set out, this means when remove the formwork all surfaces should be smooth and NO NEED TO BE PLASTERED, so that the resulting concrete product is in a right place and is of correct shape and size. N.B. The structure should be kept moist and protect from the sun for at least 10 days. | m³ | 5.6179 |  | 0
44.2 | Construction of 2 numbers of trapezoid shape reinforced concrete braces under the projection of the slab of 25cm thick with top width of 73cm and bottom width of 40cm and 30cm height reinforced with iron bars of diameter Ø16 and staffs of diameter 8mm. | m³ | 0.08475 |  | 0
| Sub total - 44 |  |  |  | 0
45 | Staircase access steps and others finishing activities
45.1 | Construction of 20cm wide 35cm thick (15cm inside of the structure and 20cm outside) of reinforced concrete supporting knee beam of the staircase of 1:2:4 mixing ratio with # 8 Y16 (4 bended and 4 straight) and staffs of 8mm@ 250mm/cc N.B. Note that the calculated quantities volume is only the lowest part of the beams (20cmx20cm) as the top part is inside of the staircase and will considered part of the staircase structure. | m³ | 0.296 |  | 0
45.2 | Construct 20cm wide 35cm thick (15cm inside of the landing slab and 20cm outside) of reinforced concrete supporting beam of 1:2:4 mixing ratio with # 6 Y16 and staffs of 6mm@ 250mm/cc . N.B. Note that the calculated quantities volume is only the lowest part of the beams (20cmx20cm) as the top part is inside of the staircase and will considered part of the staircase structure. | m³ | 0.4716 |  | 0
45.3 | Construction of reinforced concrete 1:2:4 mixing ratio staircase of 172cm width with 36 steps of 30cm trade and 15cm rise with two landing of 150cmx353cm and 15cm thick. The concrete should be reinforced with 5 pieces of straight and 5 folded iron bars diameter ∅ 16mm each ramp. Note the price will be include also the third staircase on the ground floor N.B. Note that the staircase should be protected from sun and kept moist for at least 10 days | m³ | 4.4109 |  | 0
45.4 | For ramp: Provide and fixing of handrail made by stainless steel pipes of approximately diameter Ø 50mm at the two sides of front ramps access including. The sample of the handrail has to be got approved from site engineer before fixing. | m | 19.4 |  | 0
45.5 | For the staircases: Provide and fixing of handrail made by stainless steel pipes of approximately diameter Ø 50mm for staircase including landing. The sample of the handrail has to be got approved from site engineer before fixing. | m | 14.25 |  | 0
| Sub total - 45 |  |  |  | 0
46 | Flooring
46.1 | Construction of 60cm x 60cm non slippery ceramic floor tiles for the landing of the staircase of the building laid and jointed with cement sand mortar of 1:2 mixing. Note the price will be include also the third staircase on the ground floor | m² | 17.685 |  | 0
46.2 | Construction of 60cm x 10cm ceramic skirting tiles for all bottom edge of the walls of the building laid and jointed with cement sand mortar of 1:2 mixing. | m | 31.093 |  | 0
46.3 | Construction of 60cm x 60cm non slippery local made terrazzo floor on the top surfaces of two step access outside of the building. The terrazzo should be divided by PVC or steel boundary edges with light green color. Note that the proportion of cement sand must be 1:2 mixing. | Item | 1 |  | 0
46.4 | Construction of ceramic floor marble tiles on the trade and rise of the two steps inside of the building corridor. The marble must be laid and jointed with cement sand mortar of 1:2 mixing. The sample of the marble has to be got approved from site engineer before fixing. N.B. Note that the given area is only the trades of staircase of 30cmx120cm, but the bidder should include his/her prices the budget of the rises of 15cmx120cm | m² | 17.028 |  | 0
46.5 | Construction of 140cm width along external edges of the building with floor paving made by cement sand interlocking with all required fitting and fixer such as retaining wall of cement blocks to external edges, aggregate powder to lay the floor before fixing the paving etc. Also the price should be added construction of retaining wall made by cement blocks laid and jointed with cement sand mortar of 1:6 mixing with adequate foundation wall of at least 40cm under ground. | m² | 11.004 |  | 0
| Sub total - 46 |  |  |  | 0
47 | Plastering and other decoration works
47.1 | Apply of first coat on 30mm thick plastering of cement sand mortar of 1:6 mixing ratio for all external new constructed stone wall surfaces | m² | 4.716 |  | 0
47.2 | Apply 20mm thick on internal external plastering with cement sand mortar of 1:5 mixing ratio for all new constructed wall surfaces including stone walls. | m² | 136.4118 |  | 0
47.3 | Apply on 10mm thick rough cast plastering of cement sand mortar of 1:2 mixing ratio on external 1,200mm bottom part of the windows sills of wall surfaces including the first floor. Note that the wall should be market by blocks of 52cmx26cm with lines approximately 1cm wide. | m² | 10.152 |  | 0
47.4 | Apply two coats white wash with white emulsion filler on all wall surfaces, and filling with it on all depressed area of the wall surfaces including the under ceiling with external projection of under ceiling of the slab. | m² | 173.6381 |  | 0
47.5 | Apply two coats of light yellow distemper inside and outside of building walls and white distemper on under ceiling | m² | 173.6381 |  | 0
47.6 | Apply two coats of light grey distemper paint on the rough casted surfaces at external walls of building. | m² | 10.152 |  | 0
| Sub total - 47 |  |  |  | 0
48 | Electricity
INTERIOR ELECTRICAL SERVICES
Lighting
48.1 | Type F1: 1200mm 1x18w Surface Mounted LED light fitting with CAT 2 Louvered with maximum unified glare of 19 and with LED lamp as "Thomson" LED (1x1750LM MIN)The lamp shall have a minimum of 30,000 hours lifetime; and with 50000 times switching cycles. The color temperature shall be 3000 - 7000K and luminous flux of 1500 - 1700 lumens. | Item | 2 |  | 0
48.2 | Type F1E: Ditto as Type F1 above but emergency version of 3hour duration | Item | 1 |  | 0
48.3 | Type E- 21w IP44 die-cast aluminum light fitting with clear diffuser and complete with lamp as massive Sussex CAT 81657/01/30 | Item | 2 |  | 0
48.4 | Type EXIT: 8W, Non-maintained illuminated emergency exit light sign luminaire with white steel body. Emergency lighting of 3 hour duration | Item | 3 |  | 0
| Sub total - 48 |  |  |  | 0
49 | Light Switches
49.1 | Supply, install and connect following 10A lighting switches on recessed switchboxes wired in 1.5 sq.mm PVC single core copper cables enclosed in concealed HG PVC conduits complete with all necessary accessories:
49.2 | 1 gang 1 way | Item | 1 |  | 0
49.3 | 1 gang 2 ways | Item | 2 |  | 0
49.4 | 2 gangs 2 ways | Item | 1 |  | 0
49.5 | 3 gangs 1 way | Item | 1 |  | 0
49.6 | Intermediate switch | Item | 1 |  | 0
| Sub total - 49 |  |  |  | 0
50 | Power sockets, Isolators and DP Switches
50.1 | Supply, install, test and commission the following power sockets as shown on drawing, as per the preamble, the specifications and supervision engineer's requirements.
50.2 | Supply, install and connect 13Amp standard twin socket outlets for normal power as MK or equal and approved (5numbers for each room of 6.2mx3.68m). Note that the sockets must be fixed at least 60cm from the pavement level. | Item | 2 |  | 0
50.3 | Supply, install and connect 13Amp standard twin socket outlets for normal power as MK or equal and approved for the Wi-Fi at the corridor of the building. Note that the sockets must be fixed at least 60cm from the bottom level of concrete slab. | Item | 1 |  | 0
50.4 | Supply, install and connect 15A un-switched DP outlet plate with fuse connector and neon indicator for Fire Alarm Panel power supply and marked "FACP" | Item | 3 |  | 0
50.5 | Supply, install and connect 30A switched TPN industrial isolator outlet plate with connector Split Air Conditioning Units power supply and marked "AIR CONDITIONER" respectively | Item | 1 |  | 0
| Sub total - 50 |  |  |  | 0
51 | Cables, Cable pathways and Conduits
51.1 | Supply, install, test and commission 450/750 volts 6491X cables with all required accessories for proper installation and operation including conduits, pipes( each cable in separate conduit or pipe), cable lugs, ties... etc. as shown on drawing, as per the preamble, the specifications and supervision engineer's requirements.
51.2 | Supply, install and connect complete 3x1.5 sq. mm color-coded SC cables to lighting points drawn in Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 6 |  | 0
51.3 | Supply, install and connect complete 3x2.5 sq. mm color-coded SC cables to lighting points drawn in Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 2 |  | 0
51.4 | Supply, install and connect complete 3x2.5 sq. mm color-coded SC cables to socket power points drawn in ring and within Concealed /surface 25mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 2 |  | 0
51.5 | Supply, install and connect complete 3x2.5 sq. mm color-coded SC cables to Fire Alarm Panel power points drawn in spur and within Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 3 |  | 0
51.6 | Supply, install and connect complete 3x2.5 sq. mm color-coded SC cables for Split Air Conditioning Units power supply drawn in spur and within Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 1 |  | 0
51.7 | Supply and install 4C, 50sq.mm XLPE/SWA /PVC Copper Cable from generator at West side of main entrance gate DB to new building DB' complete with cable lugs and cable glands | m | 18 |  | 0
51.8 | Excavate trench for XLPE/SWA /PVC Copper Cable not exceeding 300 mm and average 500 mm deep, part return, fill in, ram the ground (Final ground finish with direction of site engineer) | m | 10 |  | 0
51.9 | Electrical ducts and manholes |  |  |  | 0
51.1 | Supply and install the following uPVC ducts at 600mm below ground level. Rate to be inclusive of trenching at 600mm below ground level, back filling of trenches, and laying of "DANGER" cable tiling, reinstatement and making of good of ground as per directed by the site engineer: |  |  |  | 0
51.11 | a) 2x100mm uPVC duct | m | 10 |  | 0
51.12 | Construct 600mm x 600mm x 600mm deep [internal dimensions] reinforced concrete power manhole complete with heavy duty cast iron cover | Item | 8 |  | 0
| Sub total - 51 |  |  |  | 0
52 | Distribution Boards
52.1 | Supply, install, connect, testing and commission the following final distribution boards, distribution terminal blocks according to drawings, specifications and relevant codes and as Merlin Gerin or equal and approved
52.2 | Supply, install, connect-up complete 100 Amp 6way TP/N MCB Distribution Board as Merlin Gerin or equal and approved for normal power supply, for ground floor complete with integral isolator as specified | Item | 1 |  | 0
52.3 | Supply, install, and connect 100Amp, 4 way SP/N Consumer unit , as Merlin Gerin or approved equivalent, as shown on schematic wiring drawing for lightings load only | Item | 1 |  | 0
52.4 | Supply, install, test and commission miniature circuit breakers (MCBs) rated at 500Vac for above items with 10KA short circuit current according to schematics, specifications and relevant codes and as Merlin Gerin or equal and approved |  |  |  | 0
52.5 | 10A (TP)- 30mA | Item | 1 |  | 0
52.6 | 30A (TP)- 30mA | Item | 1 |  | 0
52.7 | 10A (SPN)- 30mA | Item | 1 |  | 0
52.8 | Blanking plates for items above(TP) | Item | 1 |  | 0
52.9 | Blanking plates for items above(SP) | Item | 1 |  | 0
| Sub total - 52 |  |  |  | 0
53 | Earthling
53.1 | Supply, install, test and commission Copper earthling mat for electrical system of 1200mmx1200mm dimensions constructed of 25mm x 3mm copper tape laid 1000mm deep in ground and complete with 10sq.mm earth lead cable for earthling in Masonry earth pit and with concrete removable cover marked "EARTH" | Lump Sump | 1 |  | 0
53.2 | Allow for testing and commissioning Electrical Installations | Lump Sump | 1 |  | 0
53.3 | FIRE DETECTION AND ALARM SYSTEM |  |  |  | 0
53.4 | Supply and install 1.5mm sq. fire rated copper cable for Smoke detector outlet as per layouts | Item | 3 |  | 0
53.5 | Supply and install 1.5mm sq. fire rated copper cable for Sounder outlet per layouts | Item | 1 |  | 0
53.6 | Supply and install 1.5mm sq. fire rated copper cable for Call point fire break glass unit outlet per layouts | Item | 2 |  | 0
53.7 | Supply and install complete 4-zone conventional fire alarm panel as Menvier MF9304 or equivalent by HF Fire but approved by engineer as per the specifications | Item | 1 |  | 0
53.8 | Supply and install conventional surface mounted Call point fire break glass unit as menvier MBG914 or similar but approved complete with conduit and wiring as shown on the drawings | Item | 1 |  | 0
53.9 | Supply and install conventional optical Smoke Detector / Sensors unit as Menvier MID810 or similar but approved complete with conduit and wiring a shown on the drawings | Item | 3 |  | 0
53.1 | Supply and install 93 mm diameter conventional electronic sounder as Menvier MWS424SB or similar but approved complete with wiring | Item | 1 |  | 0
53.11 | Allow for programming by THE SPECIALIST SUPPLIER of the Fire Detection and Alarm System | Lump Sump | 1 |  | 0
53.12 | Allow for TRAINING of Client personnel on the fire detection and alarm system operations | Lump Sump | 1 |  | 0
53.13 | Allow for testing and commissioning of the fire detection and alarm system | Lump Sump | 1 |  | 0
| Sub total - 53 |  |  |  | 0
54 | Air-conditions
54.1 | Provide and connection of 12,000BTU split air conditions with all required fitting and fixer | Item | 1 |  | 0
| Sub total - 54 |  |  |  | 0
55 | Doors, windows, protection bars and grab rails
55.1 | Supply and fix 220cm height, 330cm width and with panel of 6cm thick solid core, red hardwood veneer laminated door shutter with hardwood lipping all round; veneer and color to be approved. Complete with; hardwood frame, architrave, transome and all ironmongery. The sample of the door has to be got approved from site engineer. | Item | 1 |  | 0
55.2 | Provide and fix at least 100cm height stain less steel handrail made with pipes of external diameter not less than 5cm fixed at side and landing of steps of the staircase by mounting of holding poles at distance of approximately not less than 65cm c/c. N.B. The grab rail shall be capable of carrying a static load of 150 kg. | m | 14.38 |  | 0
| Sub total - 55 |  |  |  | 0
56 | Over roof
56.1 | Construct 4 pieces of 30cm x 30cm reinforced concrete columns of 280cm height Not included beams. The concrete must be 1:2:4 mixing ratio and reinforced with No. 8 Y16 and staffs of Ø 8mm @250mm c/c. N.B. Note that the columns should be protected from sun and kept moist for at least 10 days. | m³ | 1.008 |  | 0
56.2 | Construction 280cm height for staircase cabin walling of masonry cement blocks (0.40mx0.20mx0.20m) wall laid and jointed by cement sand mortar of 1:6 mixing ratio | m² | 44.713 |  | 0
56.3 | Construction of masonry cement blocks of 90cm height on the parapet wall at the front and two sides of staircase building. The wall should be made with cement blocks wall of 0.40mx0.20mx0.20m laid and jointed by cement sand mortar of 1:6 mixing ratio | m² | 20.691 |  | 0
56.4 | Construction of masonry cement blocks of approximately 58cm (20cm at the front side and 95cm at the backside) height top crown parapet wall on top of the staircase cabin. The wall should be made with cement blocks wall of 0.40mx0.20mx0.20m laid and jointed by cement sand mortar of 1:6 mixing ratio | m² | 9.9354 |  | 0
56.5 | Construction of 15cm thick and 20cm wide RC tie beam on top of final level of staircase cabin wall. The beam should be 1:2:4 mixing ratio with # 4 Y10 and staffs of 6mm@ 250mm/cc | m³ | 0.5898 |  | 0
56.6 | Ditto 10cm thick and 25cm width copping beam on top of the parapet wall of front and two sides of staircase building. | m³ | 0.57475 |  | 0
56.7 | Ditto 10cm thick and 25cm width copping beam on top of the parapet wall of staircase cabin. | m³ | 0.42825 |  | 0
56.8 | Construction of masonry cement blocks wall of 90cm height 40cm x 40cm wide to cover the iron bars on top of slab roof. The wall should be made with cement blocks wall of 0.40mx0.20mx0.20m laid and jointed by cement sand mortar of 1:6 mixing ratio. Note that the price should be included supplying of fixing to the iron bars by 6 pieces PVC pipes of diameter 3cm and 10cm height. | Item | 4 |  | 0
56.9 | Apply on 20mm thick internal external plastering of cement sand mortar of 1:5 mixing ratio for all new constructed surfaces crown parapet walls. | m² | 150.6788 |  | 0
56.1 | Apply two coats white wash with white emulsion filler on all wall surfaces, and filling with it on all depressed area of the wall surfaces including the protection iron bars of columns over the slab roof. | m² | 150.6788 |  | 0
56.11 | Apply two coats of light yellow distemper inside and outside of building wall surfaces including the protecting iron bars of columns over the slab roof and with white light grey on external edges of copping beam. | m² | 150.6788 |  | 0
| Sub total - 56 |  |  |  | 0
57 | Roofing
57.1 | Construction of mono pitch roof made with bottom chord tie beam of wooden of cross section 15cm x 2.5cm and with top chord beam by wooden of cross section 10cm x 5cm connected with rafters of cross section 10cm x 5cm. Covered on it by battens of wooden of cross section 5cmx5cm and GI sheets of 300cmx100cm | m² | 25.938 |  | 0
57.2 | Supply and fix approved suspended t & g ceiling to eaves from an approved UPVC ceiling including all necessary battens, cornices, beadings and accessories framed by steel of cross section 2"x2" distanced 600mmx600mm both side. Include also all 50cm under external roof of the building. N.B. The external projection under the roof should be ceiled with same type | m² | 25.938 |  | 0
57.3 | Supply and fix 200mm x 20mm fascia board, including two coats enamel paint | m | 4 |  | 0
| Sub total - 57 |  |  |  | 0
| Total for Construction of staircase access of the building |  |  |  | 0

## 2 open spaces & 8 toilets
S.n. | Description | Unit | QTY | Rate in $ | Amount in $
G. | Construction of two open spaces and toilets
58 | Substructure works
Excavation and Earthwork (Provisional)
58.1 | Excavation of soft soil for foundation trenches of 60cm wide and 130cm depth starting from stripped level. When construction of foundation finishes, these materials should be returning and filled around foundation, where extra surplus materials must be dumped at least 2km away from the site as per directed by UNDP engineers. | m³ | 94.1304 |  | 0
58.2 | Ditto for 24 columns footings of 120cmx120cmx186cm depth. | m³ | 64.2816 |  | 0
| Selected filling |  |  |  | 0
58.3 | Provide and compact 65cm height first layer with approved marram or other approved backfilling materials over the existing floor of whole building including the toilets inside the safe haven and server room of the building. Note that this should be filled and compacted by layers which not exceed than 15cm by layer. | m³ | 155.0003 |  | 0
58.4 | Provide and compact 30cm height hardcore layer with approved materials over the existing floor of whole building including the toilets of safe haven and server room of the building | m³ | 71.5386 |  | 0
| Anti-termite treatment |  |  |  | 0
58.5 | Provide and apply on the upper surfaces of hardcore layer a chemical spry or powder anti-termite treatment as "Premise 200 SC" or other equal and approved anti insecticide materials. | m² | 238.462 |  | 0
| Damp proof membrane |  |  |  | 0
58.6 | Provide and lay 1000-gauge polythene or other equal and approved damp proof membrane laid under surface bed with 300mm side and end laps (measured net- allow for laps) | m² | 238.462 |  | 0
| Concrete work in substructure |  |  |  | 0
58.7 | Construction of 5cm thick and 60cm wide Plain cement concrete of class 15 ( 1:3:6 mixing) under the foundation walls of the building. | m³ | 3.6204 |  | 0
58.8 | Ditto for internal subdivision wall of the toilets of 40cm wide and 5cm thick. | m³ | 0.446 |  | 0
58.9 | Ditto for 24 columns footing of 120cmx120cmx5cm depth. | m³ | 1.728 |  | 0
| Foundation Walling |  |  |  | 0
58.1 | Construction of 40cm wide and 221cm height (136cm under ground and 85cm above ground) foundation wall made by rubble stone jointed and connected by cement sand mortar of mixing ratio 1:6 | m³ | 136.9139 |  | 0
58.11 | Ditto for internal subdivision wall of the toilets of 40cm wide and 85cm height. | m³ | 7.582 |  | 0
| Sub total - 58 |  |  |  | 0
59 | Super structure works
Plain and reinforced concrete works
59.1 | Construct 120cmx120cmx40cm reinforced concrete of 1:2:4 mixing ratio for footing of the columns with 9 numbers of Y16 both ways. | m³ | 13.824 |  | 0
59.2 | Ditto for 24 columns neck of 40cm x40cm and 226cm height with 10 numbers of Y 16mm | m³ | 8.6784 |  | 0
59.3 | Construct 40cm wide, 20cm thick of reinforced concrete beam of 1:2:4 mixing ratio with # 8 Y16 and staffs of 8mm@ 250mm/cc over foundation wall including the toilets | m³ | 14.1744 |  | 0
59.4 | Laying 7cm thick plain cement concrete of 1:3:6 mixing ratio over newly constructed hardcore layer with proper finish. | m³ | 16.6923 |  | 0
59.5 | Construct 24 pieces of 30cm x 40cm reinforced concrete columns of 305cm height of the building. The concrete must be 1:2:4 mixing ratio and reinforced with No. 8 Y16 and staffs of Ø 8mm @250mm c/c. Note that the given height is not included the beams. N.B. Note that the columns should be protected from sun and kept moist for at least 10 days. | m³ | 8.784 |  | 0
59.6 | Construct 20cm wide, 15cm thick of reinforced concrete 2.2m level beam of 1:2:4 mixing ratio with # 6 Y14 and staffs of 6mm@ 250mm/cc. This is for all constructed walls including toilet. | m³ | 4.5744 |  | 0
59.7 | Construction of reinforced concrete corbel on external top edges of windows. The corbel must be constructed in three steps of 5cm height each with the top layer of 250cmx 70cm, where the second layer is 240cm x 65cm and the last layer at the bottom is 226cmx60cm, with two supporting braces (see detail drawings). The concrete should be mixed by 1:2:4 and reinforced with iron bars of diameter Ø12mm and Ø 10mm | m³ | 2.462 |  | 0
59.8 | Construct of 180 cm x 30 cm x 5cm reinforced concrete window sills at bottom edge windows for offices and toilets. The concrete should be mixed by 1:2:4 with # 3 Y12 and staffs of 8 mm @ 200mm/cc | m³ | 0.27 |  | 0
59.9 | Construction of reinforced concrete 1:2:4 mixing ratio loaded beam of 30cm width and 65cm height (15cm inside of the slab and 50cm outside). The concrete should be reinforced with 6 pieces of straight bars diameter ∅ 16mm (2 on top and 4 at the bottom), 2 pieces of bended bars diameter ∅ 16mm and 2 reinforcement bars of diameter ∅ 16mm of 300cm length on top of the columns. All these bars should be united by staffs of 8mm@ 250mm/cc. N.B. Note that the calculated quantities volume is only the lowest part of the beams (50cmx30cm) as the top part is inside of the slab and will considered part of the slab structure. | m³ | 13.68 |  | 0
59.1 | Construction of reinforced concrete 1:2:4 mixing ratio final beam (Not loaded) of 20cm width and 35cm height (15cm inside of the slab and 20cm outside). The concrete should be reinforced with 6 pieces of bars diameter ∅ 16mm with staffs of iron bars of 8mm@ 250mm/cc | m³ | 3.2192 |  | 0
| Sub total - 59 |  |  |  | 0
60 | Construction of internal steps access
60.1 | Construction of internal external steps of 30cm trade and 15cm rise made by rubble stone jointed and connected with cement sand mortar of 1:6, with 10cm plain cement concrete of 1:2:4 on top of stone base
60.2 | Stone wall basement made with ruble stone jointed and connected with cement sand mortar of 1:6 ratio. | m³ | 0.78 |  | 0
60.3 | Construction of 10cm thick of plain cement conrete of 1:2:4 mixing ratio over the stone wall | m³ | 0.3 |  | 0
60.4 | Constrution of exported marle on the steps and rise of the staitcase | m² | 3.9 |  | 0
| External acces steps in the middle: |  |  |  | 0
60.5 | For the front access steps in the middle of the two ramps: Construction of 206cm wide and 700cm length made by stone laid and jointed with cement sand mortar of 1:6 mixing. After it pour on top with 10cm thick plain cement concrete of 1:2:4 mixing ratio. Note that this steps should be kept moist and protect from the sun for at least 10 days. See the detail drawings for the rise and trades dimensions |  |  |  | 0
60.6 | Excavation of soft soil for foundation trenches of 60cm wide and 60cm depth starting from stripped level. When construction of foundation finishes, these materials should be returning and filled around foundation, where extra surplus materials must be du | m³ | 5.0184 |  | 0
60.7 | Construction of 5cm thick and 60cm wide PCC of 1:3:6 mixing ratio over the two foundation walls. | m³ | 0.4182 |  | 0
60.8 | Construction of 40cm wide and 55 cm height foundation walling over the PCC | m³ | 3.0668 |  | 0
60.9 | Construction of multi-trapezoide shape of masonry cement blocks (0.40mx0.20mx0.20m) wall laid and jointed by cement sand mortar of 1:6 mixing ratio. Note that price will be include reinforcement hoop iron made by fixing of two lines of iron bars of diameter Ø 8mm for every alternate course. N.B. Note that the given height is only the cement blocks wall which is not included the ring beams | m² | 8.5667 |  | 0
60.1 | Backfilling materials with marram or other approved materials. Note there will be 5.02 m³ left from excavation soil. | m³ | 4.4034 |  | 0
60.11 | Construction of 697cm legth, 260cm wide and 15cm height stone basement made with ruble stone jointed and connected with cement sand mortar of 1:6 ratio. | m³ | 2.7183 |  | 0
60.12 | Construction of 10cm thick of plain cement conrete of 1:2:4 mixing ratio over the trade and rise of steps and landing area | m³ | 2.1138 |  | 0
For access the two ramps at the front
60.12 | For the two front access ramp: Construction of 316cm wide and 800cm length made stone laid and jointed with cement sand mortar of 1:6 mixing. After it poured on top by 10cm thick plain cement concrete of 1:2:4 mixing ratio. Note that this ramp should be kept moist and protect from the sun for at least 10 days. |  |  |  | 0
60.13 | Excavation of soft soil for foundation trenches of the two retaining walls of 1200cm legth, 78cm wide and 60cm depth each starting from stripped level. When construction of foundation finishes, these materials should be returning and filled around foundation, where extra surplus materials must be du | m³ | 11.232 |  | 0
60.14 | Construction of 5cm thick and 60cm wide PCC of 1:3:6 mixing ratio over the two foundation walls. | m³ | 0.72 |  | 0
60.15 | Construction of trapezoid retaining stone wall of approximately 174cm height, 78cm bottom width and approximately 43cm top width over the PCC | m³ | 26.7264 |  | 0
60.16 | 43cm wide and 10cm height reinforced concrete copping beam on top of the retaining wall. The concrete must be reinforced with 4 number of iron mars of diameter Y 10 and staffed with iron bars of diameter y 8 @ 250cm c/c. | m³ | 1.032 |  | 0
60.17 | Backfilling materials with marram or other approved materials. Note there will be 11.23 m³ left from excavation soil. | m³ | 19.2444 |  | 0
60.18 | Provide and compacting of hardcore layer of 777cm length, 316cm wide and 30cm height. | m³ | 14.7319 |  | 0
60.19 | Construction of 10cm thick of plain cement concrete of 1:2:4 mixing ratio over the trade and rise of steps and landing area | m³ | 4.9106 |  | 0
| Sub total - 60 |  |  |  | 0
61 | Construction of concrete blocks
61.1 | Construction 305cm height walls of masonry cement blocks (0.40mx0.20mx0.20m) wall laid and jointed by cement sand mortar of 1:6 mixing ratio. Note that price will be include reinforcement hoop iron made by fixing of two lines of iron bars of diameter Ø 8mm for every alternate course. N.B. Note that the given height is only the cement blocks wall which is not included the ring beams | m² | 330.754 |  | 0
61.2 | Ditto for the subdivision wall of two set toilets of 285cm height. N.B. Note that the given height is only the cement blocks wall which is not included the ring beams | m² | 55.53 |  | 0
| Sub total - 61 |  |  |  | 0
62 | R.C roofing
62.1 | R.C (1:2:4 Mixing ratio) slab cover of 15cm thick with Ø 12mm main bars and 10mm distribution bars both ways at top and bottom and distanced 15cm c/c .Formwork must be accurately set out, this means when remove the formwork all surfaces should be smooth and NO NEED TO BE PLASTERED, so that the resulting concrete product is in a right place and is of correct shape and size. N.B. The structure should be kept moist and protect from the sun for at least 10 days. | m³ | 52.2293 |  | 0
62.2 | Construction of 16 numbers of trapezoid shape reinforced concrete braces under the projection of the slab of 25cm thick with top width of 73cm and bottom width of 40cm and 30cm height reinforced with iron bars of diameter Ø16 and staffs of diameter 8mm. | m³ | 0.678 |  | 0
| Sub total - 62 |  |  |  | 0
63 | Flooring
63.1 | Construction of 60cm x 60cm non slippery ceramic floor tiles for all pavement of the building laid and jointed with cement sand mortar of 1:2 mixing. Note that the price is included the floor hall, toilets and corridor. | m² | 287.182 |  | 0
63.2 | Construction of 60cm x 10cm ceramic skirting tiles for all bottom edge of the walls of the building laid and jointed with cement sand mortar of 1:2 mixing. Note that the price is included the skirting of the corridor. | m | 118.28 |  | 0
63.3 | Construction of 60cm x 60cm non slippery local made terrazzo floor on the top surfaces of the step access outside of the building. The terrazzo should be divided by PVC or steel boundary edges with light green color. Note that the proportion of cement sand must be 1:2 mixing. | Item | 1 |  | 0
63.4 | Ditto the two ramps | Item | 2 |  | 0
63.5 | Construction of ceramic floor marble tiles on the trade and rise of the main entrance gate and steps at the staircase side inside of the building corridor. The marble must be laid and jointed with cement sand mortar of 1:2 mixing. The sample of the marble has to be got approved from site engineer before fixing. N.B. Note that the given area is only the trades of staircase of 30cmx120cm, but the bidder should include his/her prices the budget of the rises of 15cmx120cm | m² | 6.38 |  | 0
63.6 | Construction of 140cm width along external edges of the building with floor paving made by cement sand interlocking with all required fitting and fixer such as retaining wall of cement blocks to external edges, aggregate powder to lay the floor before fixing the paving etc. Also the price should be added construction of retaining wall made by cement blocks laid and jointed with cement sand mortar of 1:6 mixing with adequate foundation wall of at least 40cm under ground. | m² | 56.196 |  | 0
| Sub total - 63 |  |  |  | 0
64 | Plastering and other decoration works
64.1 | Apply of first coat on 30mm thick plastering of cement sand mortar of 1:6 mixing ratio for all external new constructed stone wall surfaces | m² | 24.084 |  | 0
64.2 | Apply 20mm thick on internal external plastering with cement sand mortar of 1:5 mixing ratio for all new constructed wall surfaces including stone walls. | m² | 834.998 |  | 0
64.3 | Apply on 10mm thick rough cast plastering of cement sand mortar of 1:2 mixing ratio on external 1,200mm bottom part of the windows sills of wall surfaces including the first floor. Note that the wall should be market by blocks of 52cmx26cm with lines approximately 1cm wide. | m² | 48.168 |  | 0
64.4 | Construction of 270cm height ceramic wall tiles for all walls of the toilets laid and jointed with cement sand mortar of 1:2 mixing | m² | 182.208 |  | 0
64.5 | Apply two coats white wash with white emulsion filler on all wall surfaces, and filling with it on all depressed area of the wall surfaces including the under ceiling with external projection of under ceiling of the slab. | m² | 952.813 |  | 0
64.6 | Apply two coats of light yellow distemper inside and outside of building walls and white distemper on under ceiling | m² | 952.813 |  | 0
64.7 | Apply two coats of light grey distemper paint on the rough casted surfaces at external walls of building. | m² | 48.168 |  | 0
| Sub total - 64 |  |  |  | 0
65 | Electricity
INTERIOR ELECTRICAL SERVICES
Lighting
65.1 | Type F1: 1200mm 1x18w Surface Mounted LED light fitting with CAT 2 Louvered with maximum unified glare of 19 and with LED lamp as "Thomson" LED (1x1750LM MIN)The lamp shall have a minimum of 30,000 hours lifetime; and with 50000 times switching cycles. The color temperature shall be 3000 - 7000K and luminous flux of 1500 - 1700 lumens. | Item | 40 |  | 0
65.2 | Type F1E: Ditto as Type F1 above but emergency version of 3hour duration | Item | 20 |  | 0
65.3 | Type E- 21w IP44 die-cast aluminum light fitting with clear diffuser and complete with lamp as massive Sussex CAT 81657/01/30 | Item | 4 |  | 0
65.4 | Type 4 - 8.5w IP54 LED spherical ball light fitting complete with LED lamps for toilets | Item | 12 |  | 0
65.5 | Type EXIT: 8W, Non-maintained illuminated emergency exit light sign luminaire with white steel body. Emergency lighting of 3 hour duration | Item | 4 |  | 0
| Sub total - 65 |  |  |  | 0
66 | Light Switches
66.1 | Supply, install and connect following 10A lighting switches on recessed switchboxes wired in 1.5 sq.mm PVC single core copper cables enclosed in concealed HG PVC conduits complete with all necessary accessories:
66.2 | 1 gang 1 way | Item | 14 |  | 0
66.3 | 1 gang 2 ways | Item | 4 |  | 0
66.4 | 2 gangs 2 ways | Item | 2 |  | 0
66.5 | 3 gangs 1 way | Item | 1 |  | 0
66.6 | Intermediate switch | Item | 1 |  | 0
| Sub total - 66 |  |  |  | 0
67 | Power sockets, Isolators and DP Switches
67.1 | Supply, install, test and commission the following power sockets as shown on drawing, as per the preamble, the specifications and supervision engineer's requirements.
67.2 | Supply, install and connect 13Amp standard twin socket outlets for normal power as MK or equal and approved (5numbers for each room of 6.2mx3.68m). Note that the sockets must be fixed at least 60cm from the pavement level. | Item | 42 |  | 0
67.3 | Supply, install and connect 13Amp standard twin socket outlets for normal power as MK or equal and approved for the Wi-Fi at the corridor of the building. Note that the sockets must be fixed at least 60cm from the bottom level of concrete slab. | Item | 6 |  | 0
67.4 | Supply, install and connect 15A un-switched DP outlet plate with fuse connector and neon indicator for Fire Alarm Panel power supply and marked "FACP" | Item | 2 |  | 0
67.5 | Supply, install and connect 30A switched TPN industrial isolator outlet plate with connector Split Air Conditioning Units power supply and marked "AIR CONDITIONER" respectively | Item | 8 |  | 0
| Sub total - 67 |  |  |  | 0
68 | Cables, Cable pathways and Conduits
68.1 | Supply, install, test and commission 450/750 volts 6491X cables with all required accessories for proper installation and operation including conduits, pipes( each cable in separate conduit or pipe), cable lugs, ties... etc. as shown on drawing, as per the preamble, the specifications and supervision engineer's requirements.
68.2 | Supply, install and connect complete 3x1.5 sq. mm color-coded SC cables to lighting points drawn in Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 76 |  | 0
68.3 | Supply, install and connect complete 3x2.5 sq. mm color-coded SC cables to lighting points drawn in Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 4 |  | 0
68.4 | Supply, install and connect complete 3x2.5 sq. mm color-coded SC cables to socket power points drawn in ring and within Concealed /surface 25mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 42 |  | 0
68.5 | Supply, install and connect complete 3x2.5 sq. mm color-coded SC cables to Fire Alarm Panel power points drawn in spur and within Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 2 |  | 0
68.6 | Supply, install and connect complete 3x2.5 sq. mm color-coded SC cables for Split Air Conditioning Units power supply drawn in spur and within Concealed /surface 20mm HG PVC conduits, complete with draw boxes, switch boxes and other necessary accessories. | Item | 8 |  | 0
68.7 | Supply and install 4C, 50sq.mm XLPE/SWA /PVC Copper Cable from generator at West side of main entrance gate DB to new building DB' complete with cable lugs and cable glands | m | 200 |  | 0
68.8 | Excavate trench for XLPE/SWA /PVC Copper Cable not exceeding 300 mm and average 500 mm deep, part return, fill in, ram the ground (Final ground finish with direction of site engineer) | m | 170 |  | 0
68.9 | Electrical ducts and manholes |  |  |  | 0
68.1 | Supply and install the following uPVC ducts at 600mm below ground level. Rate to be inclusive of trenching at 600mm below ground level, back filling of trenches, and laying of "DANGER" cable tiling, reinstatement and making of good of ground as per directed by the site engineer: |  |  |  | 0
68.11 | a) 2x100mm uPVC duct | m | 170 |  | 0
68.12 | Construct 600mm x 600mm x 600mm deep [internal dimensions] reinforced concrete power manhole complete with heavy duty cast iron cover | Item | 8 |  | 0
| Sub total - 68 |  |  |  | 0
69 | Distribution Boards
69.1 | Supply, install, connect, testing and commission the following final distribution boards, distribution terminal blocks according to drawings, specifications and relevant codes and as Merlin Gerin or equal and approved
69.2 | Supply, install, connect-up complete 250 Amp 4 way TP/N main Distribution Board as Merlin Gerin or equal and approved for normal power supply, for main DB (UNSOM main switch board at back side of the building) complete with integral isolator, and 3.No 63 Amps MCCBs as specified | Item | 1 |  | 0
69.3 | Supply, install, connect-up complete 100 Amp 6way TP/N MCB Distribution Board as Merlin Gerin or equal and approved for normal power supply, for ground floor complete with integral isolator as specified | Item | 1 |  | 0
69.4 | Supply, install, and connect 100Amp, 4 way SP/N Consumer unit , as Merlin Gerin or approved equivalent, as shown on schematic wiring drawing for lightings load only | Item | 1 |  | 0
69.5 | Supply, install, test and commission miniature circuit breakers (MCBs) rated at 500Vac for above items with 10KA short circuit current according to schematics, specifications and relevant codes and as Merlin Gerin or equal and approved |  |  |  | 0
69.6 | 10A (TP)- 30mA | Item | 1 |  | 0
69.7 | 30A (TP)- 30mA | Item | 12 |  | 0
69.8 | 10A (SPN)- 30mA | Item | 1 |  | 0
69.9 | Blanking plates for items above(TP) | Item | 1 |  | 0
69.1 | Blanking plates for items above(SP) | Item | 1 |  | 0
| Sub total - 69 |  |  |  | 0
70 | Earthling
70.1 | Supply, install, test and commission Copper earthling mat for electrical system of 1200mmx1200mm dimensions constructed of 25mm x 3mm copper tape laid 1000mm deep in ground and complete with 10sq.mm earth lead cable for earthling in Masonry earth pit and with concrete removable cover marked "EARTH" | Lump Sump. | 1 |  | 0
70.2 | Allow for testing and commissioning Electrical Installations | Lump Sump. | 1 |  | 0
70.3 | FIRE DETECTION AND ALARM SYSTEM |  |  |  | 0
70.4 | Supply and install 1.5mm sq. fire rated copper cable for Smoke detector outlet as per layouts | Item | 12 |  | 0
70.5 | Supply and install 1.5mm sq. fire rated copper cable for Sounder outlet per layouts | Item | 3 |  | 0
70.6 | Supply and install 1.5mm sq. fire rated copper cable for Call point fire break glass unit outlet per layouts | Item | 4 |  | 0
70.7 | Supply and install complete 4-zone conventional fire alarm panel as Menvier MF9304 or equivalent by HF Fire but approved by engineer as per the specifications | Item | 1 |  | 0
70.8 | Supply and install conventional surface mounted Call point fire break glass unit as menvier MBG914 or similar but approved complete with conduit and wiring as shown on the drawings | Item | 4 |  | 0
70.9 | Supply and install conventional optical Smoke Detector / Sensors unit as Menvier MID810 or similar but approved complete with conduit and wiring a shown on the drawings | Item | 12 |  | 0
70.1 | Supply and install 93 mm diameter conventional electronic sounder as Menvier MWS424SB or similar but approved complete with wiring | Item | 3 |  | 0
70.11 | Allow for programming by THE SPECIALIST SUPPLIER of the Fire Detection and Alarm System | Lump Sump. | 1 |  | 0
70.12 | Allow for TRAINING of Client personnel on the fire detection and alarm system operations | Lump Sump. | 1 |  | 0
70.13 | Allow for testing and commissioning of the fire detection and alarm system | Lump Sump. | 1 |  | 0
| Sub total - 70 |  |  |  | 0
71 | Air-conditions
71.1 | Provide and connection of 18,000BTU split air conditions with all required fitting and fixer | Item | 12 |  | 0
| Sub total - 71 |  |  |  | 0
72 | Doors, windows, protection bars and grab rails
72.1 | For server room and hall: Supply and fix 215cm height, 90cm width and with panel of 6cm thick solid core, red hardwood veneer laminated door shutter with hardwood lipping all round; veneer and color to be approved. Complete with; hardwood frame, architrave, transome and all ironmongery including self closure device. The sample of the door has to be got approved from site engineer. | Item | 4 |  | 0
72.2 | For toilets: Supply and fix 210cm height, 80cm width exported hardwood timber of Singapore model complete with all fitting and fixer. The sample of the door has to be got approved from site engineer. | Item | 8 |  | 0
72.3 | For two open spaces: Provide and fix 280cm height, 300cm width and with panel of 6cm thick solid core, red hardwood veneer laminated door shutter with hardwood lipping all round; veneer and color to be approved. Complete with; hardwood frame, architrave, transome and all ironmongery including self closure device. The sample of the door has to be got approved from site engineer. | Item | 2 |  | 0
72.4 | For main entrance gate: Provide and fix 180cm height, 220cm width and with panel of 6cm thick solid core, red hardwood veneer laminated door shutter with hardwood lipping all round; veneer and color to be approved. Complete with; hardwood frame, architrave, transome and all ironmongery including self closure device. The sample of the door has to be got approved from site engineer. | Item | 1 |  | 0
72.5 | Provide and fix new double wings PVC framed windows of 150cm width and 120cm height with 6mm thick ordinary glasses and good quality nylon netting including all fittings, fixtures like hinges, handle, lock with very strong fisher and screws for fixing to the walls etc. The sample of the windows must be got approved from site engineer. N.B. Note that the ordinary glasses should be covered by not less than 6µ thick blast resistant films (BRF) with all required fitting and fixer such as adhesive sealing rubber etc. | m² | 18 |  | 0
72.6 | Provide and fix 150cm x 120cm new protection steel flowered decorated model windows bars made by angle iron frame of 20x20x3mm with another frame made by flat iron @ 200mm both ways. Finally provide and fix inside of every square by flowers of flat iron 10mmx2mm with all required fitting, fixer and two coats of antirust paint (See attached detail drawings). | m² | 18 |  | 0
72.7 | Provide and fix one grab rail fixed on each of both the inner and outer surfaces of the cubicle door; which shall not be less than 32 mm and not more than 40 mm in external diameter. The grab rail shall have a grip space of not less than 30 mm clear of each door surface. | Item | 4 |  | 0
72.8 | Provide and fix one folding grab rail on the wide side of the cubicle adjacent to the water-closet (W.C) at a height between 725mm to 750mm above the finished floor level when lowered from the wall. N.B. The folding grab rail shall be capable of carrying a static load of 150 kg. | Item | 2 |  | 0
72.9 | Provide and fix at least two grab rails which shall not be less than 32 mm and not more than 40 mm in external diameter and shall be fixed on the wall leaving a grip space of not less than 30 mm clear of the mounting wall. The two grab rails constructed in one continuous piece is acceptable. The length of grab rail shall not be less than 600 mm. N.B. The grab rail shall be capable of carrying a static load of 150 kg. | Item | 4 |  | 0
| Sub total - 72 |  |  |  | 0
73 | Sanitary system
73.1 | Supply and fix one set of European flash complete ( WC, hand wash, shower with plate etc.) with all required accessory such as mirror, toilet paper holder, towel holder, soap holder etc. | Item | 8 |  | 0
| Sub total - 73 |  |  |  | 0
74 | Connection and manhole construction & misc. items
74.1 | Construction of 1.0mx1.0 masonry cement blocks manholes laid by cement sand mortar of 1:4 with connection PVC pipes of Ø150mm diameter. The item includes all necessary excavation, cement block masonry, cover slab (1:2:4) with nominal reinforcement, plastering and finishing etc. complete as per UNDP engineers satisfaction. | Item | 12 |  | 0
74.2 | Provide and fix all required plumbing material such as height pressure PVC of diameter Ø 1½" feeder pipes from nearest available water source near of the compound, with all required fittings (Elbows, T-joints, regulator valves etc.). The price should include excavation of trench and fixing | Item | 1 |  | 0
| Sub total - 74 |  |  |  | 0
75 | Over roof
75.1 | Construction of medium 6cm (10cm and 2cm to the two edges) thick 1:4 cement sand mortar with adequate slope to the direction of points where is PVC for rain water collections | m³ | 20.8917 |  | 0
75.2 | Provide and cover with tarmac paper for 1m². This activity consists: a. Cleaning the surfaces; b. applying two coats of primer Emulsion (MW) paint; c. Providing of first quality green colored tarmac paper with fine aggregate on top; d. burning of tarmac paper by special equipment designed to burn. | m² | 348.195 |  | 0
75.3 | Provide and fix PVC of diameter Ø 11cm to 4 points where is recommended the site Engineer probably attached to reinforced concrete columns for surrounding walls of the building | Item | 6 |  | 0
75.4 | Construction of masonry cement blocks of 90cm height top crown parapet wall. The wall should be made with cement blocks wall of 0.40mx0.20mx0.20m laid and jointed by cement sand mortar of 1:6 mixing ratio | m² | 67.59 |  | 0
75.5 | Construction of 10cm thick and 20cm wide RC copping beam on top of crown parapet wall. The beam should be 1:2:4 mixing ratio with # 4 Y10 and staffs of 6mm@ 250mm/cc | m² | 1.502 |  | 0
75.6 | Construction of masonry cement blocks wall of 90cm height 40cm x 40cm wide to cover the iron bars on top of slab roof. The wall should be made with cement blocks wall of 0.40mx0.20mx0.20m laid and jointed by cement sand mortar of 1:6 mixing ratio. Note that the price should be included supplying of fixing to the iron bars by 6 pieces PVC pipes of diameter 3cm and 10cm height. | Item | 24 |  | 0
75.7 | Apply on 20mm thick internal external plastering of cement sand mortar of 1:5 mixing ratio for all new constructed surfaces crown parapet walls. | m² | 160.16 |  | 0
75.8 | Apply two coats white wash with white emulsion filler on all wall surfaces, and filling with it on all depressed area of the wall surfaces including the protection iron bars of columns over the slab roof. | m² | 199.78 |  | 0
75.9 | Apply two coats of light yellow distemper inside and outside of building wall surfaces including the protection iron bars of columns over the slab roof and with white light grey on external edges of copping beam. | m² | 199.78 |  | 0
| Sub total - 75 |  |  |  | 0
| Total for two open space and 8 toilets of new NIEC building near of MIA |  |  |  | 0

## Septic tank
S.n. | Description | Unit | QTY | Rate in $ | Amount in $
H. | Construction of main septic tank of the compound
76 | Substructure works
76.1 | Excavation of soft soil for septic tank of 900cm x 1,100cm and 345cm depth starting from stripped level. When construction of foundation and walls finishes, these materials should be returning and filled around foundation, where extra surplus materials must be dumped at least 2km away from the site as per directed by UNDP engineers. Note that this excavation can be used either manpower or machinery. | m³ | 341.55 |  | 0
76.2 | Ditto soak pit of 240cm x 966cm and 300cm depth | m³ | 69.552 |  | 0
76.3 | Soak pit cornice wall: Excavation of soft soil for foundation trenches of 80cm wide and 60cm depth starting from stripped level. When construction of wall finishes, these materials should be returning and filled around foundation, where extra surplus materials must be dumped at least 2km away from the site as per directed by UNDP engineers. | m³ | 11.5776 |  | 0
76.4 | Ditto for the six (3 inlet and 3 outlet) manholes of 140cmx100cmx90cm depth. | m³ | 7.56 |  | 0
76.5 | Construction of 5cm thick Plain cement concrete of class 15 ( 1:3:6 mixing) under the floor basement of the septic tank of the compound. | m³ | 4.95 |  | 0
76.6 | Ditto cornice walling of soak pit of 80cm width and 5cm thick around the top edge. | m³ | 0.9648 |  | 0
76.7 | Ditto for the six (3 inlet and 3 outlet) manholes of 140cmx100cmx5cm depth. | m³ | 0.42 |  | 0
76.8 | R.C (1:2:4 Mixing ratio) floor foundation slab of 880cm x 1,046cm 15cm thick with Ø 12mm main bars and 10mm distribution bars both ways at top and bottom and distanced 15cm c/c. N.B. The structure should be kept moist and protect from the sun for at least 10 days. | m³ | 13.8072 |  | 0
76.9 | Ditto for the six (3 inlet and 3 outlet) manholes of 140cmx100cm15cm depth. | m³ | 1.26 |  | 0
76.1 | Construction of 40cm wide and 300cm height septic tank wall made by rubble stone jointed and connected by cement sand mortar of mixing ratio 1:6 | m³ | 52.44 |  | 0
76.11 | Ditto for 40cm wide and 55cm height stone walling at top cornice of soak pit. | m³ | 5.6584 |  | 0
76.12 | Construction of cement blocks walling of the six manholes made with cement blocks of 40cmx20cmx20cm laid and jointed with cement sand mortar of 1:6 mixing ratio. | m² | 15.3 |  | 0
76.13 | Construct 40cm wide, 15cm thick of reinforced concrete beam at 150cm height level of 1:2:4 mixing ratio with # 8 Y16 and staffs of 8mm@ 250mm/cc over septic tank wall including the middle subdivision wall. | m³ | 2.8188 |  | 0
| Sub total - 76 |  |  |  | 0
77 | Super structure works
77.1 | Provide and fixing of traditional brush wooden of approximately Ø 8cm diameter and 300cm height or other equal steel structure such as ITP- 80mmx30mmx3mm or angle iron of 80mmx80mmx3mm. The poles should be laid horizontally on the top surfaces of the soak pit at distance 116cm c/c | Item | 10 |  | 0
77.2 | Provide and fixing of GI sheets covering of 240cm x 120cm and 1.5mm thick over the wooden or steel poles on top of the soak pit | Item | 12 |  | 0
77.3 | Soak pit: Covering and laying on the GI by 1000-gauge polythene or other equal and approved damp proof membrane laid under surface bed with 300mm side and end laps (measured net- allow for laps) | m² | 33.472 |  | 0
77.4 | Soak pit: Covering on top of the polythene by pre-excavated soil from the soak pit | Item | 1 |  | 0
77.5 | Construct 40cm wide, 20cm thick of reinforced concrete beam ring at final level of the wall of 1:2:4 mixing ratio with # 6Y16 and staffs of 8mm@ 250mm/cc over septic tank wall including the middle subdivision wall. | m³ | 3.7584 |  | 0
77.6 | Provide and compact the gap between septic tank walling and the ground with the pre-excavated soil, pouring and compacting by layers which not exceed than 15cm by layer. | Item | 1 |  | 0
77.7 | Provide and pouring of clean broken natural hardcore in the soak pit of 240cm width 966cm length and 300cm height. | m³ | 69.552 |  | 0
| Sub total - 77 |  |  |  | 0
78 | R.C roofing
78.1 | R.C (1:2:4 Mixing ratio) slab cover of 15cm thick with Ø 12mm main bars and 10mm distribution bars both ways at top and bottom and distanced 15cm c/c. Note that there will be four access iterance with same concrete and with adequate handles of iron bars of diameter Ø 14mm. N.B. The structure should be kept moist and protect from the sun for at least 10 days. | m³ | 13.8072 |  | 0
78.2 | Ditto for the six (3 inlet and 3 outlet) manholes of 140cmx100cmx15cm depth. | m³ | 1.26 |  | 0
| Sub total - 78 |  |  |  | 0
79 | Flooring
79.1 | Plastering with 2cm thick screed cement sand mortar of 1:2 mixing ration on all floor surfaces of the septic tank. | m² | 77.28 |  | 0
79.2 | Ditto the three manholes floors of 60cm x 100cm | m² | 4.32 |  | 0
| Sub total - 79 |  |  |  | 0
80 | Plastering, plumbing & other finishing works
80.1 | Apply of first coat on 3cm thick plastering of cement sand mortar of 1:6 mixing ratio for all internal constructed stone wall surfaces of the septic tank | m² | 141.84 |  | 0
80.2 | Apply 2cm thick on internal plastering with screed cement sand mortar of 1:2 mixing ratio for all internal septic tank wall surfaces. | m² | 141.84 |  | 0
80.3 | Ditto internal wall surfaces of the six manhole | m² | 16.2 |  | 0
80.4 | Provide and fix three inlet PVC pipes of diameter Ø 11cm diameter and approximately 180cm length | m | 5.4 |  | 0
80.5 | Ditto three outlet three inlet PVC pipes of diameter Ø 11cm diameter and approximately 750cm length note that this is included the pipes of soak pit | m | 22.5 |  | 0
80.6 | Provide and three inlet PVC junction single plain of diameter Ø 11cm diameter and with approximately 50cm length PVC pipes of diameter 11cm with all required fitting and fixer including holding braces. | Item | 3 |  | 0
80.7 | Ditto the three outlet PVC junction single plain of diameter Ø 11cm with all required fitting and fixer including holding braces. | Item | 3 |  | 0
80.8 | Provide and fix 12 numbers (six pieces each side) of steps access made by 50cm wide with two braces of 50cm (25 inside the wall and 25 above wall surfaces) GI pipes of diameter Ø 5cm with all required fitting and fixer. | Item | 12 |  | 0
80.9 | Provide and three inlet PVC smell pipes of diameter Ø 8cm diameter and 200cm height with all required fitting and fixer including holding braces. | Item | 2 |  | 0
| Sub total - 80 |  |  |  | 0
| Total for construction of sharing septic tank of new NIEC building near of MIA |  |  |  | 0

## Power house
S.n. | Description | Unit | QTY | Rate in $ | Amount in $
I. | Construction of power house
81 | Substructure works
Excavation and Earthwork (Provisional)
81.1 | General cleaning for all broken stones, trees, sharps and other material which are the area where is going to be build the building . | m² | 70 |  | 0
81.2 | Room: Excavation of foundation trenches of 60cm wide and 80cm depth. Excavated material should be used backfilling for the base of the building it self. | m³ | 12.864 |  | 0
81.3 | 2 Ramps: Excavation of soft soil for foundation base of of 300cm legth, 250cm wide and 20cm depth each ramp starting from stripped level. | m³ | 3 |  | 0
| Selected filling |  |  |  | 0
81.4 | Room: Provide and compact 50cm height 480cm wide and 740cm legth hardcore layer with approved materials over the floor of the generator room | m³ | 17.76 |  | 0
81.5 | Ditto: 2 Ramps of 20cm height 300cm length and 250width | m³ | 3 |  | 0
| Anti-termite treatment |  |  |  | 0
81.6 | Room: Provide and apply on the upper surfaces of hardcore layer a chemical spry or powder anti-termite treatment as "Premise 200 SC" or other equal and approved anti insecticide materials. | m² | 35.52 |  | 0
81.7 | Ditto : 2 Ramps | m² | 15 |  | 0
| Damp proof membrane |  |  |  | 0
81.8 | Room: Provide and lay 1000-gauge polythene or other equal and approved damp proof membrane laid under surface bed with 300mm side and end laps (measured net- allow for laps) | m² | 35.52 |  | 0
81.9 | Ditto 2 ramps | m² | 15 |  | 0
| Concrete work in substructure |  |  |  | 0
81.1 | Room: Construction of 5cm thick Plain cement concrete of 1:3:6 mixing of 60cm wide | m³ | 0.804 |  | 0
81.11 | 2 Ramps: Construction of 60cm height, 300cm length and 250cm width Plain cement concrete of class 15 ( 1:3:6 mixing) over the two ramps | m³ | 4.5 |  | 0
81.12 | Construct 40cm wide, 15cm thick of reinforced concrete beam of 1:2:4 mixing ratio with # 6 Y14 and staffs of 6mm@ 250mm/cc over foundation wall | m³ | 1.608 |  | 0
| Sub total - 81 |  |  |  | 0
82 | Foundation Walling and other works
82.1 | Construction of 120cm height (75cm under ground and 45cm above ground) foundation wall made by masonry cement blocks (0.40mx0.20mx0.20m) wall laid and jointed by cement sand mortar of 1:6 mixing ratio. Note that price will be include reinforcement hoop iron made by fixing of two lines of iron bars of diameter Ø 8mm for every alternate course. N.B. Note that the given height is only the cement blocks wall which is not included the ring beams | m² | 32.16 |  | 0
82.2 | Provide and fixing in the stone walling of 14 pieces GI pipes poles of 100mm diameter. See the attached drawing for height and the way of fixing the pipes | Item | 14 |  | 0
| Sub total - 82 |  |  |  | 0
83 | Super structure works
Concrete work in substructure
83.1 | Room: Laying 10cm thick plain cement concrete of 1:2:4 mixing ratio over newly constructed hardcore layer with proper finish. | m³ | 3.8 |  | 0
83.2 | Construct two 185cm wide, 380cm and 20cm height of reinforced concrete engine basement of 1:2:4 mixing ratio with Y12 mm@ 100mm/cc both ways | m³ | 2.812 |  | 0
| Sub total - 83 |  |  |  | 0
84 | Construction of concrete blocks and other works
84.1 | Construction of 100cm height masonry cement ventilation blocks (40cmx20cmx20cm) wall laid and jointed by cement sand mortar of 1:5 mixing ratio | m² | 21.8 |  | 0
84.2 | Supply and weld with strong rhomboid type chicken mesh on the angle iron of 30mmx30mmx3mm covering with steel plate of 3mmx2mm | m² | 25.4639 |  | 0
| Sub total - 84 |  |  |  | 0
85 | Plastering and other finishing
85.1 | Apply on 30mm thick plastering of cement sand mortar of 1:6 mixing ratio for on external new constructed stone wall surfaces | m² | 16.08 |  | 0
85.2 | Apply on 20mm thick plastering of cement sand mortar of 1:5 mixing ratio for all new constructed wall surfaces | m² | 16.08 |  | 0
85.3 | Internal external pointing of the jointing area with cement sand mortar of 1:5 mixing ratio. Note the given area is the total area of the wall but the pointing surfaces. | m² | 43.6 |  | 0
85.4 | Apply two coats white wash with wood glue fix for all wall surfaces | m² | 59.68 |  | 0
85.5 | Apply two coats of light yellow distemper inside and outside of building walls | m² | 59.68 |  | 0
85.6 | Apply two coats of green oil paint for all steel structure including GI poles, chicken mesh and angle iron . | m² | 25.4639 |  | 0
| Sub total - 85 |  |  |  | 0
86 | Roofing
86.1 | Construction of gable end prepainted Gauge 28 roof made with bottom chord tie beam of wooden of cross section 15cm x 2.5cm and with top chord beam by wooden of cross section 10cm x 5cm connected with rafters of cross section 10cm x 5cm. Covered on it by battens of wooden of cross section 5cmx5cm and GI sheets of 300cmx100cm | m² | 43.2 |  | 0
| Sub total - 86 |  |  |  | 0
87 | Doors
87.1 | Provide and fix 2.37m height and 2.50m width double wings steel door made with external frame of steel hallow box of 80mmx40mmx2mm, covered to the lowest 1.00m by steel plate of 1.5mm thick and for upper part with steel hallow box of 25mmx25mmx1mm distanced vertically a gap of 100mm each to another, with all necessary fittings, fixtures, handles and locks. The rate shall include all fittings, fixtures, and painting complete. The sample of the door has to be got approved from site engineer. | Item | 2 |  | 0
| Sub total - 87 |  |  |  | 0
| Total for construction of generator room |  |  |  | 0

## Basement for 2 tents
S.n. | Description | Unit | QTY | Rate in $ | Amount in $
J. | Construction of tents basement
86 | Substructure works
Excavation and Earthwork (Provisional)
86.1 | General cleaning for all broken stones, trees, sharps and other material which are the area where is going to be build the building . | m² | 900 |  | 0
86.2 | Excavation of foundation basement bed of 30m x 15m and 0.2m depth. Excavated material should be used backfilling for the base of the building it self. | m³ | 90 |  | 0
| Selected filling |  |  |  | 0
86.3 | Provide and compact 20cm height hardcore layer with approved materials over the existing floor of whole tent basement | m³ | 180 |  | 0
| Anti-termite treatment |  |  |  | 0
86.4 | Provide and apply on the upper surfaces of hardcore layer a chemical spry or powder anti-termite treatment as "Premise 200 SC" or other equal and approved anti insecticide materials. | m² | 900 |  | 0
| Damp proof membrane |  |  |  | 0
86.5 | Provide and lay 1000-gauge polythene or other equal and approved damp proof membrane laid under surface bed with 300mm side and end laps (measured net- allow for laps) | m² | 900 |  | 0
| Sub total - 86 |  |  |  | 0
87 | Superstructure
87.1 | Construct two 30m x 15m and 20cm height of reinforced concrete tents basement of 1:2:4 mixing ratio with Y12 mm@ 100mm/cc both ways | m³ | 180 |  | 0
| Sub total - 87 |  |  |  | 0
| Total for construction of two tent basements floor |  |  |  | 0

## Summary
Summary for construction of Data center three open spaces toilets safe and server rooms for NIEC in Mogadishu- Somalia
# | Description of activity | Budget in US $
A. | Site cleaning preparation activities | 0
B. | Construction of retaining wall at north side of the building | 0
C. | Sitting up and construction of protection hoarding wall | 0
D. | Construction of Data center hall with screening room and toilets | 0
E. | Construction of one open space server room and safe haven | 0
F. | Construction of staircase access of the building | 0
G. | Construction of two open spaces and toilets | 0
H. | Construction of main septic tank of the compound | 0
I. | Construction of power house | 0
J. | Construction of tents basement | 0
| Grand total for construction of NIEC building near of MIA gavel road | 0