Technical Compliance Sheet

Al-Shifaa’ Medical Complex – Oncology hospital

*Note:

-This document should be read in conjunction with technical specification, in case there is any information not mentioned in this document, contractor shall refer to technical specification.

-All transformer parameters/specifications shall be in accordance with local electrical company regulations, D26 and Iraqi technical specifications for electrical works.

1-Distribution Transformer 11/0.416 kV 1250 KVA

| No | Description | Consultant specification | Offered specification |
| --- | --- | --- | --- |
| 1 | Make/Brand/Model: | to be completed by the tenderer |  |
| 2 | Name of manufacturer | to be completed by the tenderer |  |
| 3 | Type: | Oil-immersed hermetically sealed - bolted type |  |
| 4 | Country of origin | to be completed by the tenderer |  |
| 5 | Reference standard | IEC 60076-1, 2,3,5,8, IEC 60214, IEC 60137, Latest IEC standard. To be subjected by National Iraqi ministry of Electricity D026. |  |
| 6 | Ambient temperature: | -Highest maximum (in the shade) +55C for about 6 hrs. a day. -Lowest minimum –10C. -Maximum yearly average+30C -Maximum daily average +40C. |  |
| 7 | Air humidity: | -Maximum 92% at 40 C -Minimum 12% -Yearly average 44% |  |
| 8 | Altitude: | 1000M above sea level |  |
| 9 | Number of poles | 3 |  |
| 10 | Indoor or outdoor | Indoor |  |
| 11 | Highest system voltage | 12 kV |  |
| 12 | Short circuit current on 11 kV side | 25 KA. |  |
| 13 | Short circuit current on LV side | According to the short circuit level of H.T side and the rated power of the transformer |  |
| 14 | 11 kV system | 3- phase,3-wire with neutral isolated but provision is made for earthling through an earthling resistance of 21.1 ohms to limit the earth fault current to 300 Amp |  |
| 15 | Low voltage side earthing | Neutral solidly earthed |  |
| 16 | Low voltage side | Nominal voltage: 416/240 volts s System. 3-phase, 4-wire neutral solidly earthed. |  |
| 17 | Voltage Ratio | 11/0.416 KV |  |
| 18 | Type of cooling | ONAN |  |
| 19 | Rated power - Continuous | 1250 kVA |  |
| 20 | Rated Frequency | 50Hz |  |
| 21 | Impedance voltage at 75 deg at nominal tap | to be completed by the tenderer |  |
| 22 | Nominal Voltage of winding a) H.V. | 11 kV |  |
|  | b) L.V | 0.416 kV |  |
| 23 | Rated voltage at no load | H.V. 11kv L.V- 416 volt. |  |
| 24 | No Load losses (KW) | to be completed by the tenderer |  |
| 25 | Load loss at full load at 75 deg temperature (KW) | to be completed by the tenderer |  |
| 26 | Warranty period | two year |  |
| 27 | Efficiency | ≥ 98.9% |  |
| 28 | Winding type | copper winding, wound, 3-phase |  |
| 29 | Vector relation ship | Dyn 11 |  |
| 30 | Interphase Connection | H.V. Delta L.V- star with neutral brought out |  |
| 31 | Temperature rise. | ( i ) 45 C in top oil by thermometer (ii) 50 C in winding by resistance |  |
| 32 | No. of outgoing halls | To be an adequate number to suit the number of outgoing L.V cables |  |
| 33 | Off circuit tapings | five tapping for ± 2.5% , ± 5% % on the H.T winding for off circuit operation externally. The machine must be of the robust and definite position type with a click indicating position arrived during tap changing |  |
| 34 | Transformer oil |  |  |
| 1 | Type of oil | IEC60296 class 1 |  |
| 2 | Manufacturer | to be completed by the tenderer |  |
| 3 | Place of manufacture | to be completed by the tenderer |  |
| 4 | Manufacturer’s type designation | to be completed by the tenderer |  |
| 5 | Applied IEC standard | IEC 60296 |  |
| 6 | Kinematic viscosity mm2/s | to be completed by the tenderer |  |
|  | At 40 deg | ≤ 16.5 |  |
|  | At -15 deg | ≤ 800 |  |
| 7 | Flash point | ≥ 140 C |  |
| 8 | Pour point | ≤ - 30 C |  |
| 9 | Density at 20 deg C – kg/dm3 | ≤ 0.895 |  |
| 10 | Breakdown strength (kV) | to be completed by the tenderer |  |
| 35 | Thickness of transformer a) tank b) sides c) bottom | Minimum 3 mm Minimum 3 mm Minimum 3 mm |  |
| 36 | Thickness of radiator plates and for cooling tube | mm |  |
| 37 | Noise level at 0.3 m distance | ≤ 55 dB |  |
| 38 | Type of corrosion protection on steel parts a) Inside tank b) Outside tank | Oil resistant paint Metalized, aluminum paint or equivalent |  |
| 39 | 11 kV bushings |  |  |
| 1 | Name of manufacturer | to be completed by the tenderer |  |
| 2 | Make/Brand/Model: | to be completed by the tenderer |  |
| 3 | Reference standard | IEC 60137 |  |
| 4 | Type of bushing | to be completed by the tenderer |  |
| 5 | Rated current (Amp) | to be completed by the tenderer |  |
| 6 | Rated voltage (KV) | to be completed by the tenderer |  |
| 7 | Material | Porcelain |  |
| 8 | Color | Brown |  |
| 9 | Creepage distance (mm) | to be completed by the tenderer |  |
| 37 | L.V bushings |  |  |
| 1 | Name of manufacturer | to be completed by the tenderer |  |
| 2 | Make/Brand/Model: | to be completed by the tenderer |  |
| 3 | Reference standard | IEC 60137 |  |
| 4 | Type of bushing | to be completed by the tenderer |  |
| 5 | Rated current (Amp) | to be completed by the tenderer |  |
| 6 | Rated voltage (KV) | to be completed by the tenderer |  |
| 7 | Material | Porcelain |  |
| 8 | Color | Brown |  |
| 9 | Creepage distance in (mm) | to be completed by the tenderer |  |
| 38 | Warranty period | two year |  |
| 39 | Submit type test certificates or reports: |  |  |
| 40 | Submit Detail drawings, drawings of HV and LV bushings, details of accessories, brochures and catalogues: |  |  |

- Non extensible Ring Main Unit, (Indoor Type Switch gear, 630A, 11 kV)

*Note:

All Ring Main Unit parameters/specifications shall be in accordance with local electrical company regulations, D07 and Iraqi technical specifications for electrical works.

| No | Description | Consultant specification | Offered specification |
| --- | --- | --- | --- |
| 1 | Make/Brand/Model: | to be completed by the tenderer |  |
| 2 | Name of manufacturer | to be completed by the tenderer |  |
| 3 | Type: | Non-extensible Vacuum or SF6 insulated Ring Main Unit |  |
| 4 | Country of origin | to be completed by the tenderer |  |
| 5 | Reference standard | IEC 62271-200 IEC 62271-105 IEC 62271-102 IEC 62271-100 IEC 60265-1 IEC 60044-1 IEC 60044-2 Latest IEC standard and to be subjected by National Iraqi ministry of Electricity D07. Note: Successful tenderer shall submit two copies of IEC standards. |  |
| 6 | Ambient temperature: | - Highest maximum (in the shade) : + 55 °C - Lowest minimum: -10 °C - Maximum yearly average: + 30 °C - Maximum daily average: + 40 °C |  |
| 7 | Air humidity: | - Maximum 92% at 40°C - Minimum 12% - Yearly average 44% |  |
| 8 | Altitude: | From sea level up to (1000m) |  |
| 9 | Rated Frequency | 50Hz |  |
| 10 | Indoor or outdoor | Indoor |  |
| 11 | Service Voltage | 11 KV |  |
| 12 | Highest system voltage | 12 kV |  |
| 13 | Short circuit level | 25 KA r.m.s 11kV |  |
| 14 | Impulse withstand voltage | 75 KV |  |
| 15 | One minute power frequency withstand voltage | 28 KV |  |
| 16 | 11 kV system | 3- phase, 3 wire with neutral isolated but provision is made for earthing in future through earthing resistance of 21.1 ohms to limit the earth fault current to 300 amps |  |
| 17 | The degree of protection of persons against hazardous approach to live parts | (IP40) |  |
| 18 | Earthing Device of Switch Gear | Preferable to be built in type shall be provided for earthing the cable feeder (fault earthing switch). |  |
| 19 | The Load Break Switch of Switch Gear | (Non – automatic) suitable for use in conjunction with circuit breaker panels and switch fuses to form compost extensible switchboards. The switch to be of a single break type having on, off and earth positions with quick make and break features in all positions. |  |
| 20 | Fuse Switch | The fuse switches should be hand operated totally enclosed in line with switch panel. The fuse switch shall be of sf6 gas sealed chamber interrupters. The fuse switch shall be triple pole with provisions for automatic tripping in case of failure of any fuse also reclosing cannot be carried out unless the burnt fuse is replaced. |  |
| 21 | Fuses | Fuse links should be current limiting and should comply with IEC 60282. The successful tenderer will be required to select the rated current and time/current characteristics of fuse link as described under clause 21.2 of IEC 60282. The tenderer will also be required to furnish the purchaser with the time/current characteristics and rating of the circuit breaker which has to be used on the L.T. side of the transformer according to H.V. fuses selected by the tenderer in order to afford correct discrimination. |  |
| 22 | Protection and Instrument Transformers of the Switch Gear | - Protection Relays: Shall be flush mounting type, designed for tropical climate, IP 50, capable of carrying continuously the full load current Instrument Transformers: A- Current Transformers: Must comply with IEC 60185, and 60044 cast resin insulated. The secondary winding of the current transformer shall be designed for a rated current of 5 A. for metering shall be of class accuracy (0.5) and 15VA burden. B -Voltage Transformer: Must comply with IEC 60186, and 60044. It should be of 50VA class (1) and protected by means of easily accessible fuses and both H.V & L.V sides. The secondary voltage shall be 110 V between phases. C- Earth Fault Indication: The position of this indicator shall be at load break isolator. These indications are to be RED lamps indicators, or any other alternative solutions. The design must be suitable for this arrangement. |  |
| 23 | Warranty period | Two years |  |

3-Generator Sets

*Note: This document should be read in conjunction with technical specification “SECTION 16620: GENERATOR SET SYSTEM SND AUTOMATIC TRANSFER SWITCH”, in case there is any information not mentioned in this document, contractor shall refer to technical specification.

3-1    Generator Set 1250 KVA

3-1-1Complete Gen Set – 1250 KVA Prime Power

| Description | Consultant specification | Offered specification |
| --- | --- | --- |
| Make/model No: | To be Provided |  |
| Name of complete gen set manufacturer | Cummins, caterpillar, Volvo, or equivalent - Original manufacturer (Local Assembled Not acceptable) |  |
| Ambient temperature: | Maximum:55/C Minimum:-10/C |  |
| Relative Humidity: | 92% maximum |  |
| Altitude: | 1000M above sea level |  |
| System Voltage: | 400V ,Wye connected |  |
| No of phase: | 3PH |  |
| Frequency: | 50Hz |  |
| Fuel type | Diesel |  |
| Guarantee: | 2 Years |  |
| Generator output Range | 1250 KVA Prime power |  |
| Main circuit breaker | 2000 Amp ACB, 4 poles with current adjustment setting |  |
| Daily tank | 5000lt. Free stand tank for 8 hours continuous running |  |
| Submit Detail drawing brochure catalogue | To be Provided |  |
| Power factor | Not less than 0.8 |  |
| Noise Level from the whole set : | Below 85 dB at a distance of 1 meter. |  |
| IP | Not less than 44 |  |

3-1-2-ENGINE

| Description | Consultant specification | Offered specification |
| --- | --- | --- |
| Make/model No: | To be Provided |  |
| Name of manufacturer of engine | Cummins, caterpillar, , Volvo, or equivalent - Original manufacturer (Local Assembled Not acceptable) |  |
| Engine Equipment | equipped with air filters, fuel filters and pressure gauge, lubricating oil cooler, filters, and pressure gauge, water pump and temperature gauge, service hour meter, flywheel, and flywheel housing when applicable ,and all other needed accessories . |  |
| RPM: | 1500 |  |
| Prime power | 1250 KVA |  |
| Type of Governor: | Electronic |  |
| Overload rating: | as per International standard |  |
| Fuel filter : | Standard water separator filter |  |
| Type of fuel : | Diesel |  |
| Type of starting | 24Volt DC |  |
| Type of cooling: | Radiator–fan cooled–fan to be driven by the engine shaft. |  |
| Exhaust System | The exhaust silencer shall be a high attenuation residential type, sized and supplied by the engine supplier. It shall provide 20-30 dBA attenuation while imposing no more than 6.7 kPa (27 in H2O) restriction, with drain cock. |  |
| Wiring and Conduit | multi-strand annealed copper conductors encased by cross-linked polyethylene insulation resistant to heat, abrasion, oil, water, antifreeze, and diesel fuel. Wiring shall be suitable for continuous use at 120C (250F) with insulation not brittle at -50C (-60F). |  |
| Guaranteed fuel consumption/hour at 100 % load | To be Provided |  |
| Submit Detail drawing brochure catalogue | To be Provided |  |

3-1-3- ALTERNATOR

| Description | Consultant specification | Offered specification |
| --- | --- | --- |
| Type Make/ model No: | To be Provided |  |
| Name of manufacturer of alternator | Cummins, caterpillar, , Volvo, or equivalent - Original manufacturer (Local Assembled Not acceptable) |  |
| Rated Voltage : | 400V |  |
| Rated power factor : | between 0.8 and 1 |  |
| No. of Phase : | 3Ph |  |
| Frequency: | 50Hz |  |
| Type of excitation: | Brushless, self-excited/permanent magnet rotating field brushless. |  |
| Percentage regulation : | +-1% |  |
| Insulation type : | Class H |  |
| AVR type : | digital |  |
| Submit Detail drawing brochure catalogue : | To be Provided |  |

3-1-4-CONTROL PANEL

| UNDP specifications | Consultant specification | Offered specification |
| --- | --- | --- |
| Make/model No: | To be Provided |  |
| Name of manufacturer- | Cummins, caterpillar, , Volvo, or equivalent - Original manufacturer (Local Assembled Not acceptable) |  |
| Controller information - | Metering equipment:- AC voltage 3 phase. AC amps. KW KVA KVAR PF Frequency DC Voltage Coolant temperature. Oil pressure RPM Hours run Controls Auto start / stop. Emergency stop Phase selector switch Voltage control Shut down annunciation. Low oil pressure High coolant temperature Over speed Overcrank Indicating lights Emergency stop Fault shutdown Fault alarms Protective relaying Over/under voltage Reverse power relay Over/under frequency Over current |  |
| Submit Detail drawing brochure catalogue: | To be Provided |  |

3-1-5-ATS controller

| Description | Consultant specification | Offered specification |
| --- | --- | --- |
| Make: Model number: | To be Provided |  |
| Name of manufacturer | Cummins (USA). Caterpillar (UK). Mitsubishi (Japan). Volvo (Sweden). Approved equivalent |  |
| Country of origin | Cummins (USA). Caterpillar (UK). Mitsubishi (Japan). Volvo (Sweden). Approved equivalent |  |
| Mounting | Floor |  |
| Enclosure material | Galvanized sheet steel cubicle |  |
| Rating | 2000A |  |
| Poles | 4 pole |  |
| Voltage | 400V |  |
| Control instrument | Circuit breakers/contactors Voltage sensing control relay Auxiliary switch Indicating lightings |  |
| Technical details and catalogues | To be Provided |  |

” SECTION 16710: FIRE ALARM SYSTEM “, in case there is any information not mentioned in this document, contractor shall refer to technical specification.

4. Fire alarm System

| Description | Consultant specification | Offered Requirement |
| --- | --- | --- |
| Make/model No: | To be submitted |  |
| Manufacturer: | Simplex (US). Notifier (UK). Edward (UK). Approved equal. *Note: All equipment used in the system shall, as far as practicable, be designed and provided by single manufacturer. |  |
| Standards | NFPA 72, NFPA 101 Local civil defense authorities requirements |  |
| Environment | Temperature: 0-50C Humidity: 0 to 93% non-condensing |  |
| Communication network | The system shall be of Multi-Priority, token passing, peer-to-peer network wired as Class A. A loop type network shall be provided by connecting each panel in series starting from and ending at the same panel. Any defective device in the detection loop shall be automatically bypassed without affecting the normal function of the rest of the system. The network shall be capable of connecting 50 panels per secured network. |  |
| Loops | Reliability: A fault in any one loop shall not interrupt the operation of other loops. Capacity: minimum 125 addressable devices per loop. Distance: maximum 1 KM length for loop. |  |
| Display | General display shall incorporate an assigned area for each detector indication with LED indicator for each area arranged in accordance with manufacturers standard design A display diagram shall be provided. The diagram shall include a representation of the building(s) with a clear display of all areas covered by the fire alarm system including the details of building entrances; circulation areas escape routes, and the division of loops. |  |
| Alarm signals | Fault warning sound level: at least 5 dBA above the average ambient sound level in the area of fault. Sound level of fault warning sounders at operator location shall be minimum 70 dB(A). Alarm sounders sound level: at least 75 dBA at 3 meter but not more than 120 dBA, and at least 15 dBA above the average ambient sound level in the area of alarm High noise area requirements: combined horn and strobe units for alarm, and sounders shall operate in frequency range of 600 to 1000 Hz. Looping: Sounders shall be installed/wired in detector loops or on separate sounder circuits, as per the approved manufacturer’s standard. |  |
| Fire Alarm Control Panel | No. of loops: F.A.C.P-1 :6 Loops. F.A.C.P-2 :6 Loops. Standard : UL listed Connection:peer-to-peer network connection Wiring classification: Class-A Degree of protection: minimum IP-30 Mounting: recessed mounted. Location: as per design drawings and to be coordinated with site condition (approval of site engineer is required). Power Supply: 230V, 50Hz Battery back-up: 24 stand-by, and 3 hours emergency operation. Keys: control, function, acknowledge, display action, enter keys Indicators: power on, common alarm, common fault, CPU fail indicators. Interface: shall be compatible with interfacing with other systems/equipments (mechanical equipments, security racks, voice evacuation racks). Printer to be included Auxiliary power output: to connect the repeater panel to the main fire alarm panel by the means of microprocessor based data communication system. |  |
| Smoke detector | Type: analogue addressable Standard: UL or BS 5445:part7 Sensor operation: optical smoke sensors shall imply the forward light-scatter principle using optical components, and shall have high resistance to contamination and corrosion. Protection: shall be encapsulated in high resistively epoxy resin. Indicator: LED indicator, to provide indication of alarm actuation. |  |
| Heat sensors | Type: analogue addressable Standard: UL or BS 5445:part5 and 8. Sensor operation: shall employ two heat sensing elements with different thermal characteristics to provide rate of rise dependent response. Protection: shall be encapsulated in high resistively epoxy resin. Indicator: LED indicator, to provide indication of alarm actuation. |  |
| Manual Call Points | Type: analogue addressable Standard: BSEN54 or UL listed Operation: by thumb pressure Protection: shall be capable of having a weatherproof cover with IP-66. Alarm response time: less than 1 second. Indicator: LED indicator, to provide indication of alarm actuation. |  |
| Control module | Type: analogue addressable Power: 24volt, 1 amp. |  |
| Monitor module | Type: analogue addressable Power feeding: from the addressable loop directly. |  |
| Line isolator module | Power feeding: from the addressable loop directly. Indicator: LED indicator. |  |
| Graphic terminal | A PC based GCC (Graphic Command Central) shall be installed. to monitor and control all of the points within the entire Network. |  |
| Conduits type | Rigid steel type ( if exposed) Nonmetallic rigid PVC (embedded or above false ceiling). Conduit type to be approved by the engineer and in accordance with local civil defense requirements. |  |
| Cables | Fire resistant armored cable low smoke and fume (60 minutes). Cables type to be approved by the engineer and in accordance with design drawings and local civil defense requirements. |  |
| Warranty | 2 years . |  |
| Shop drawings submittal | Detailed shop drawings shall be submitted by the contractor/system specialist. |  |