## Lighting Details Sorted by Zone
Ref # | Zone | Floor Name / Number | Room Name/ Number | Equipment Type (LED, Fluorescent, incandescent) | Tube Type (T5, T8, etc) | Fixture Length | # of Fixtures | Tubes per Fixture | No of Tubes/ bulbs | Power /bulb-tube (W) | Inst'lld Power (W) | Week day usage, Hrs/day | Weekend usage, hrs/day | Total Usage kWHrs/Week | # of switches in room | Number of switches per fixture | Control Type | Ballast Type (Electronic, Magnetic)
3 | Admin Building | Ground | Females Bathroom | Fl. | Bulb | n/a | 1 | 1 | 1 | 100 | 100 | 4 | 4 | 2.8 | 1 | 1 | Switch | Electronic
2 | Admin Building | Ground | Corridor | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 12 | 12 | 5.04 | 1
8 | Admin Building | First | Corridor | Fl. | T12-2 | 2 | 6 | 2 | 12 | 20 | 240 | 3 | 3 | 5.04 | 1 | 1 | Switch | Electronic
26 | Admin Building | First | CEO Dining Room | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 | 1 | 1 | Switch | Magnetic
27 | Admin Building | First | Bathroom | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 | 1 | 1 | Switch | Magnetic
4 | Admin Building | Ground | Lobby Area | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 6 | 6 | 1.68 | 2 | 1 | Switch | Magnetic
7 | Admin Building | Ground | Corridor | Fl. | T12-2 | 2 | 4 | 2 | 8 | 20 | 160 | 3 | 3 | 3.36 | 2 | 1 | Switch | Electronic
17 | Admin Building | Ground | Males Bathroom | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 4 | 4 | 1.12 | 1 | 1 | Switch | Electronic
18 | Admin Building | Ground | Photo-copy Room | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 0 | 1.6 | 1 | 1 | Switch | Electronic
36 | Admin Building | Ground | Passage | Fl. | T12-2 | 2 | 2 | 2 | 4 | 20 | 80 | 12 |  | 4.8 | 1 |  | Switch | Electronic Ballast
44 | Admin Building | Ground | Male Bathroom | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 3 |  | 0.6 | 1 |  | Switch | Electronic Ballast
45 | Admin Building | Ground | Male Bathroom | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 3 |  | 0.6 | 1 |  | Switch | Electronic Ballast
46 | Admin Building | Ground | Female Bathroom | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 3 |  | 0.6 | 1 |  | Switch | Electronic Ballast
47 | Admin Building | Ground | Female Bathroom | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 3 |  | 0.6 | 1 |  | Switch | Electronic Ballast
54 | Admin Building | Ground | Nurses sign in office | Fl. | T12-2 | 4 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24
37 | Admin Building | Ground | Passage | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 |  | 9.6 | 1 |  | Switch | Electronic Ballast
19 | Admin Building | First | Oper-ations Officer 1 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 3 | 0 | 2.4 | 1 | 1 | Switch | Magnetic
21 | Admin Building | First | Senior Medical Officer Secretary | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 0 | 3.2 | 1 | 1 | Switch | Electronic
22 | Admin Building | First | Senior Medical Officer | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 0 | 3.2 | 1 | 1 | Switch | Electronic
23 | Admin Building | First | Chief Executive Officer | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 0 | 6.4 | 1 | 1 | Switch | Magnetic
24 | Admin Building | First | Hospital Admin Secretary | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 0 | 3.2 | 2 | 1 | Switch | Magnetic
25 | Admin Building | First | Hospital Admin Office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 3 | 0 | 1.2 |  | 1 | Switch | Electronic
6 | Admin Building | Ground | Reception Area | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 24 | 24 | 26.88 | 2 | 1 | Switch | Electronic
9 | Admin Building | Ground | Director of Nursing Services Secretary | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 0 | 3.2 | 1 | 1 | Switch | Magnetic
10 | Admin Building | Ground | Director of Nursing Services Secretary | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 0 | 1.6 | 1 | 1 | Switch | Electronic
11 | Admin Building | Ground | Director of Nursing Services | Fl. | T12-4 | 4 | 2 | 1 | 2 | 40 | 80 | 8 | 0 | 3.2 | 1 | 1 | Switch | Magnetic
12 | Admin Building | Ground | Director of Nursing Services Lunch Room | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 0 | 1.6 | 1 | 1 | Switch | Magnetic
13 | Admin Building | Ground | Deputy Director of Nursing Services | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 0 | 3.2 | 1 | 1 | Switch | Electronic
14 | Admin Building | Ground | Deputy Director of Nursing Services | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 0 | 3.2 | 1 | 1 | Switch | Magnetic
15 | Admin Building | Ground | Human Resource Depart-ment | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 8 | 0 | 12.8 | 1 | 1 | Switch | Electronic
16 | Admin Building | Ground | Human Resource Manager | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 0 | 3.2 | 1 | 1 | Switch | Electronic
28 | Admin Building | Ground | Accounts Depart-ment | Fl. | T12-4 | 4 | 5 | 2 | 10 | 40 | 400 | 11 |  | 22 | 1 |  | Switch | Electronic Ballast
30 | Admin Building | Ground | Director Of Finance Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 11 |  | 4.4 | 1 |  | Switch | Electronic Ballast
31 | Admin Building | Ground | Director Of Finance Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 11 |  | 4.4 | 1 |  | Switch | Electronic Ballast
32 | Admin Building | Ground | Salary Super-visor's Office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 11 |  | 4.4 | 1 |  | Switch | Electronic Ballast
33 | Admin Building | Ground | Salary Super-visor's Office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 11 |  | 4.4 | 1 |  | Switch | Electronic Ballast
34 | Admin Building | Ground | Computer Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 4 | 5.44 | 1 |  | Switch | Electronic Ballast
35 | Admin Building | Ground | Computer Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 4 | 5.44 | 1 |  | Switch | Electronic Ballast
38 | Admin Building | Ground | Passage | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 |  | 4.8 | 1 |  | Switch | Electronic Ballast
42 | Admin Building | Ground | Registry Room | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 3 |  | 3.6 | 1 |  | Switch | Electronic Ballast
43 | Admin Building | Ground | Registry Room | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 3 |  | 3.6 | 1 |  | Switch | Electronic Ballast
48 | Admin Building | Ground | Cashier Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 11 |  | 4.4 | 1 |  | Switch | Electronic Ballast
20 | Admin Building | First | Oper-ations Officer 2 | Fl. | T8-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 0 | 6.4 | 1 | 1 | Switch | Electronic
57 | B Ward | First | Staff bathroom | Incandescent | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 2 | 2 | 0.84 | 1
60 | B Ward | First | Chemical room | Fl. | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 |  | 1.6 | 1
61 | B Ward | First | Staff room 2 | Fl. | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 | 1
65 | B Ward | First | Treatment room | Fl. | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 12 | 12 | 3.36 | 1
69 | B Ward | First | Loiter room | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 | 1
70 | B Ward | First | Staff room 1 | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 12 | 8 | 3.04 | 1
59 | B Ward | First | Store room | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 2 | 2 | 0.56 | 1
63 | B Ward | First | Patients’ pantry | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 2 | 2 | 0.56 | 1
66 | B Ward | First | Patients’ bathroom | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 2 | 2 | 0.56 | 1
56 | B Ward | First | Main Area | Fl. | T8-2 | 2 | 4 | 2 | 8 | 20 | 160 | 8 | 8 | 8.96 | 1
58 | B Ward | First | Patients’ clothes room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 | 1
62 | B Ward | First | Pantry | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 2 | 2 | 1.12 | 1
64 | B Ward | First | Patients’ pantry | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 2 | 2 | 0.28 | 1
67 | B Ward | First | verandah | Fl. | T8-2 | 2 | 3 | 2 | 6 | 20 | 120 | 12 | 12 | 10.08 | 1
68 | B Ward | First | verandah | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 12 | 12 | 1.68
78 | Bougain-villea | Ground | Examin-ation room | Fl. | bulb | n/a | 1 | 1 | 1 | 60 | 60 | 12 | 12 | 5.04 | 1
79 | Bougain-villea | Ground | Room 9 - 13 | Fl. | bulb | n/a | 1 | 1 | 1 | 60 | 60 | 8 | 8 | 3.36 | 1
80 | Bougain-villea | Ground | Room 1-2 | Fl. | bulb | n/a | 1 | 1 | 1 | 60 | 60 | 8 | 8 | 3.36 | 1
86 | Bougain-villea | Ground | Bath Room 1 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 36 | 36 | 8 | 8 | 2.016 | 2
93 | Bougain-villea | Ground | Bathroom 3 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 36 | 36 | 8 | 8 | 2.016 | 1
88 | Bougain-villea | Ground | Bath Room 4 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 36 | 36 | 8 | 8 | 2.016 | 2
94 | Bougain-villea | Ground | Lobby | Fl. | T12-4 | 4 | 3 | 2 | 6 | 36 | 216 | 12 | 12 | 18.144 | 1
81 | Bougain-villea | Ground | Patients Bath Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 | 1
82 | Bougain-villea | Ground | Clothes room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 2 | 2 | 1.008 | 1
83 | Bougain-villea | Ground | Nurse Station | Fl. | T12-4 | 4 | 2 | 2 | 4 | 36 | 144 | 12 | 12 | 12.096 | 2
90 | Bougain-villea | Ground | Corridor | Fl. | T12-4 | 4 | 14 | 2 | 28 | 36 | 1008 | 12 | 12 | 84.672 | 1
73 | Bougain-villea | Ground | Nurse Station | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 12 | 12 | 6.048 | 1
74 | Bougain-villea | Ground | Lunch room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 | 1
75 | Bougain-villea | Ground | Bath Room/Change Room | Fl. | T12-4 | 4 | 2 | 2 | 4 | 36 | 144 | 2 | 2 | 2.016 | 2
76 | Bougain-villea | Ground | Bath Room/Change Room | Fl. | T12-4 | 4 | 1 | 1 | 1 | 36 | 36 | 2 | 2 | 0.504 | 1
77 | Bougain-villea | Ground | Treatment room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 12 | 12 | 6.048 | 1
84 | Bougain-villea | Ground | Nurse Station | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 12 | 12 | 6.72 | 2
92 | Bougain-villea | Ground | Bathroom 2 | Fl. | T8-2 | 2 | 6 | 2 | 12 | 20 | 240 | 8 | 8 | 13.44 | 1
85 | Bougain-villea | Ground | Bath Room 3 | Fl. | T8-2 | 2 | 2 | 1 | 2 | 20 | 40 | 8 | 8 | 2.24 | 2
87 | Bougain-villea | Ground | Bath Room 4 | Fl. | T8-2 | 2 | 2 | 1 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1
91 | Bougain-villea | Ground | Room1-8 | Fl. | T8-2 | 2 | 8 | 2 | 16 | 20 | 320 | 8 | 8 | 17.92 | 1
95 | CSSD | Ground | CSSD office | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 0 | 6.4 | 1 |  | Manual | Magnetic
96 | CSSD | Ground | CSSD room 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 3 | 0 | 1.08 | 1 |  | Manual | Magnetic
97 | CSSD | Ground | CSSD bathroom | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 1 | 0 | 0.4 | 1 |  | Manual | Magnetic
105 | Day clinic | Ground | Room 1 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 |  | 6.4 | 1
99 | Day clinic | Ground | Doctor's room 3 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 6 |  | 2.4 | 1 |  | Manual | Electronic
100 | Day clinic | Ground | Kitchen | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 |  | 4.8 | 1
106 | Day clinic | Ground | Doctor's room 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1 |  | Manual | Electronic
107 | Day clinic | Ground | Doctor's room 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1 |  | Manual | Electronic
110 | Day clinic | Ground | Doctors Room 4 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1
112 | Day clinic | Ground | Bath Room 1&3 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 |  | 6.4 | 1
101 | Day clinic | Ground | Kitchen | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 |  | 4.8 | 1
111 | Day clinic | Ground | Doctors Room 4 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 | 1
113 | Day clinic | Ground | Bath Room 2 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 | 1
108 | Day clinic | Ground | Corridor | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 | 1 |  | Manual | Electronic
134 | Dietary | Ground | Boiler Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 | 1
136 | Dietary | Ground | Dietitic Technician | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 | 1
141 | Dietary | Ground | Office 2 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6
115 | Dietary | Ground | Dietitian’s office | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 |  | 2.88 | 1
116 | Dietary | Ground | Bathroom (m) | Fl. | T8-4 | 4 | 2 | 2 | 4 | 36 | 144 | 8 | 8 | 8.064 | 1
117 | Dietary | Ground | Locker room | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 2 | 2 | 1.008 | 1
118 | Dietary | Ground | Bathroom (f) | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 | 1
119 | Dietary | Ground | Provision stores office | Fl. | T8-4 | 4 | 2 | 2 | 4 | 36 | 144 | 2 | 2 | 2.016 | 1
120 | Dietary | Ground | Store room | Fl. | T8-4 | 4 | 2 | 2 | 4 | 36 | 144 | 2 | 2 | 2.016 | 3
121 | Dietary | Ground | Lunch room | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 | 1
122 | Dietary | Ground | Provision cold storage 1 | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 2 | 2 | 1.008 | 1
123 | Dietary | Ground | Provision cold storage 2 | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 2 | 2 | 1.008 | 1
124 | Dietary | Ground | Provision cold storage 3 | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 2 | 2 | 1.008 | 1
125 | Dietary | Ground | Loading bay Passage | Fl. | T8-4 | 4 | 3 | 2 | 6 | 36 | 216 | 2 | 2 | 3.024 | 1
126 | Dietary | Ground | Bakery | Fl. | T8-4 | 4 | 2 | 2 | 4 | 36 | 144 | 8 | 8 | 8.064 | 1
127 | Dietary | Ground | Liquid meal center | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 12 | 12 | 6.048 | 1
128 | Dietary | Ground | Meal Preparation Area | Fl. | T8-4 | 4 | 5 | 2 | 10 | 36 | 360 | 12 | 12 | 30.24 | 1
129 | Dietary | Ground | Dietitian’s office | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 |  | 2.88 | 1
130 | Dietary | Ground | Main Serving Area | Fl. | T8-4 | 4 | 21 | 2 | 42 | 36 | 1512 | 8 | 8 | 84.672 | 1
131 | Dietary | Ground | Serving Area | Fl. | T8-4 | 4 | 2 | 2 | 4 | 36 | 144 | 12 | 12 | 12.096 | 1
132 | Dietary | Ground | Passage | Fl. | T8-4 | 4 | 2 | 2 | 4 | 36 | 144 | 12 | 12 | 12.096 | 1
133 | Dietary | Ground | Room | Fl. | T8-4 | 4 | 2 | 2 | 4 | 36 | 144 | 8 | 8 | 8.064 | 1
135 | Dietary | Ground | Boiler Room | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 2 | 2 | 1.008 | 1
137 | Dietary | Ground | Kitchen/ | Fl. | T8-4 | 4 | 3 | 2 | 6 | 36 | 216 | 12 | 12 | 18.144 | 1
138 | Dietary | Ground | Store room | Fl. | T8-4 | 4 | 3 | 2 | 6 | 36 | 216 | 2 | 2 | 3.024 | 1
139 | Dietary | Ground | Passage way | Fl. | T8-4 | 4 | 1 | 1 | 1 | 36 | 36 | 12 | 12 | 3.024 | 1
140 | Dietary | Ground | Office 1 | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 |  | 2.88 | 1
142 | Dietary | Ground | Security Area | Fl. | T8-4 | 4 | 2 | 2 | 4 | 36 | 144 | 12 | 12 | 12.096 | 1
143 | Dietary | Ground | Pump Room | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 2 | 2 | 1.008 | 1
146 | Doctor's Lounge | Ground | Passage | Fl. | T12-2 | 2 | 2 | 2 | 4 | 20 | 80 | 8 |  | 3.2 | 1 |  | Switch | Electronic Ballast
145 | Doctor's Lounge | Ground | Kitchen | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1 |  | Switch | Electronic Ballast
147 | Doctor's Lounge | Ground | Bathroom 1 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 |  | 1.6 | 1 |  | Switch | Electronic Ballast
148 | Doctor's Lounge | Ground | Room 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1 | 1 | Switch | Electronic Ballast
149 | Doctor's Lounge | Ground | Room 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1 | 1 | Switch | Electronic Ballast
150 | Doctor's Lounge | Ground | Lounge | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 |  | 6.4 | 1 | 1 | Switch | Electronic Ballast
151 | Doctor's Lounge | Ground | Restroom | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 4 | 4 | 1.12 | 1 | 1 | Switch
153 | Eastern division office | Ground | Main office | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 8 | 8 | 13.44 | 1 |  | Manual | Magnetic
154 | Eastern division office | Ground | Bed Room 1-2 | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 8 | 8 | 13.44 | 2 |  | Manual | Magnetic
155 | Eastern division office | Ground | Bed Room 3 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 | 2 |  | Manual | Magnetic
156 | Eastern division office | Ground | Bathroom | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 | 1 |  | Manual | Magnetic
159 | Emergency Area | Ground | Bathroom | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1 | 1 | Switch | Electronic Ballast
160 | Emergency Area | Ground | Change Nurse Office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1 | 1 | Switch | Electronic Ballast
162 | Emergency Area | Ground | Doctors Room | Fl. | T12-4 | 4 | 5 | 2 | 10 | 40 | 400 | 12 | 12 | 33.6 | 1 | 1 | Switch
163 | Emergency Area | Ground | Treatment Room | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 | 1 | 1 | Switch
161 | Emergency Area | Ground | Corridor | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 | 1
158 | Emergency Area | Ground | Staff Lunch Room | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 8 | 8 | 4.48 | 1 | 1 | Switch | Electronic Ballast
165 | Hibiscus 1 | Ground | Dining area | Fl. | T12-4 | 4 | 8 | 2 | 16 | 36 | 576 | 12 | 12 | 48.384 | 1
172 | Hibiscus 1 | Ground | Treatment room | Fl. | T12-4 | 4 | 2 | 2 | 4 | 36 | 144 | 12 | 12 | 12.096
175 | Hibiscus 1 | Ground | Room 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 | 1
179 | Hibiscus 1 | Ground | Lunch Room | Fl. | T12-4 | 4 | 2 | 2 | 4 | 36 | 144 | 12 | 12 | 12.096
181 | Hibiscus 1 | Ground | Passage | Fl. | T12-4 | 4 | 3 | 2 | 6 | 36 | 216 | 12 | 12 | 18.144
183 | Hibiscus 1 | Ground | Corridor | fl. | T12-4 | 4 | 2 | 2 | 4 | 36 | 144 | 12 | 12 | 12.096
166 | Hibiscus 1 | Ground | Patients bathroom | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 8 | 8 | 4.48 | 1
167 | Hibiscus 1 | Ground | Clothes room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 | 1
168 | Hibiscus 1 | Ground | Staff pantry | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 2 | 2 | 0.28 | 1
169 | Hibiscus 1 | Ground | Storage room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 | 1
170 | Hibiscus 1 | Ground | Chemical room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 | 1
171 | Hibiscus 1 | Ground | Temp Store room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 | 1
173 | Hibiscus 1 | Ground | Multi-purpose room | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 2 | 2 | 1.12 | 1
174 | Hibiscus 1 | Ground | Nurses’ change room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1
176 | Hibiscus 1 | Ground | Room 2 - 5 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1
177 | Hibiscus 1 | Ground | Staff bathroom | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1
178 | Hibiscus 1 | Ground | Shower Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1
180 | Hibiscus 1 | Ground | Passage | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 12 | 12 | 6.72
182 | Hibiscus 1 | Ground | Corridor | Fl. | T8-2 | 2 | 6 | 2 | 12 | 20 | 240 | 12 | 12 | 20.16 | 1
184 | Hibiscus 2 | Ground | Pantry | Fl. | T12-4 | 4 | 1 | 1 | 1 | 36 | 36 | 2 | 2 | 0.504 | 1
185 | Hibiscus 2 | Ground | Ward | Fl. | T12-4 | 4 | 6 | 2 | 12 | 36 | 432 | 12 | 12 | 36.288 | 1
186 | Hibiscus 2 | Ground | Patients’ pantry | Fl. | T12-4 | 4 | 5 | 2 | 10 | 36 | 360 | 2 | 2 | 5.04 | 1
188 | Hibiscus 2 | Ground | Nurses Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 12 | 12 | 6.048 | 3
189 | Hibiscus 2 | Ground | Patients bathroom | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 | 1
191 | Hibiscus 2 | Ground | Passage | Fl. | T12-4 | 4 | 5 | 2 | 10 | 36 | 360 | 12 | 12 | 30.24 | 1
187 | Hibiscus 2 | Ground | Nurses Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36 | 2
190 | Hibiscus 2 | Ground | Clothes room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 | 1
209 | In-service education 1 | Ground | Confer-ence room bathroom | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 3 |  | 0.9 | 1 |  | Manual | Magnetic
208 | In-service education 1 | Ground | Pharmacy bathroom | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 3 |  | 1.2 | 1 |  | Manual | Magnetic
198 | In-service education 1 | Ground | room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 4 |  | 1.6 | 1 |  | Manual | Electronic
200 | In-service education 1 | Ground | Passage | Fl. | T12-4 | 4 | 1 | 2 | 2 | 39 | 78 | 8.5 |  | 3.315 | 1 |  | Manual | Electronic
201 | In-service education 1 | Ground | Patient services secretary's office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8.5 |  | 3.4 | 2 |  | Manual | Electronic
202 | In-service education 1 | Ground | Pharmacy | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 8 |  | 12.8 | 1 |  | Manual | Electronic
203 | In-service education 1 | Ground | Pharmacy kitchen | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 |  | 6.4 | 1 |  | Manual | Electronic
204 | In-service education 1 | Ground | Pharmacy store room | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 8 |  | 9.6 | 2 |  | Manual | Electronic
205 | In-service education 1 | Ground | Conference room | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 5 |  | 8 | 3 |  | Manual | Magnetic
206 | In-service education 1 | Ground | Confer-ence room back/ | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 1 |  | 1.6 | 1 |  | Manual | Magnetic
207 | In-service education 1 | Ground | storage | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 1 |  | 1.6 | 1 |  | Manual | Magnetic
210 | In-service education 1 | Ground | In-service bathroom | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 3 |  | 1.2 | 1 |  | Manual | Magnetic
193 | In-service education 2 | Ground | Library | Bulb | Bulb | n/a | 4 | 1 | 4 | 60 | 240 | 8 |  | 9.6 | 1
194 | In-service education 2 | Ground | Office | Fl. | Bulb | n/a | 3 | 1 | 3 | 60 | 180 | 6 |  | 5.4 | 3 |  | Manual | Electronic
195 | In-service education 2 | Ground | Lecture Room | Fl. | Bulb | n/a | 2 | 1 | 2 | 60 | 120 | 4 |  | 2.4 | 1 |  | Manual | Electronic
196 | In-service education 2 | Ground | room | Fl. | Bulb | n/a | 2 | 1 | 2 | 60 | 120 | 4 |  | 2.4 | 1 |  | Manual | Electronic
199 | In-service education 2 | Ground | Kitchen | Fl. | Bulb | n/a | 2 | 1 | 2 | 60 | 120 | 4 |  | 2.4 | 1 |  | Manual | Electronic
197 | In-service education 2 | Ground | Lecture Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 4 |  | 0.8 | 1 |  | Manual | Electronic
215 | Laundry | Ground | Passage 2 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 | 12 | 13.44 | 1
217 | Laundry | Ground | Washing Area | Fl. | T12-4 | 4 | 12 | 2 | 24 | 40 | 960 | 8 | 8 | 53.76 | 1
214 | Laundry | Ground | Passage 1 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36 | 1
216 | Laundry | Ground | Room 1 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1
212 | Laundry | Ground | Laundry male bathroom | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 3 | 3 | 0.84 | 1 |  | Manual | Electronic
213 | Laundry | Ground | Laundry female bathroom | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 3 | 3 | 0.84 | 1 |  | Manual | Electronic
219 | Laundry | Ground | Passage 3 | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 12 | 12 | 26.88 | 1
220 | Laundry | Ground | Room 2 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 | 1
221 | Laundry | Ground | Room 3 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 | 1
222 | Laundry | Ground | Office 1-3 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
223 | Laundry | Ground | Kitchen | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 | 1
224 | Laundry | Ground | Bath Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1
225 | Maintenance | Ground | General store 1 -2 | Fl. | T12-4 | 4 | 8 | 1 | 8 | 40 | 320 | 12.5 | 12.5 | 28 | 2 |  | Manual | Magnetic
226 | Maintenance | Ground | General store 1 -2 | Fl. | T12-4 | 4 | 4 | 1 | 4 | 40 | 160 | 12.5 | 12.5 | 14 | 1 |  | Manual | Magnetic
227 | Maintenance | Ground | Bobber | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 12.5 | 12.5 | 3.5 | 1 |  | Manual | Magnetic
228 | Maintenance | Ground | Maintenance office 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12.5 | 12.5 | 7 | 1 |  | Manual | Magnetic
230 | Maintenance | Ground | work shop | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 8 | 8 | 17.92 | 1 |  | Manual | Electronic
231 | Maintenance | Ground | work shop | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 8 | 8 | 17.92 | 1 |  | Manual | Electronic
232 | Maintenance | Ground | Maintenance office 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1 |  | Manual | Electronic
233 | Maintenance | Ground | Maintenance office 1 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 | 1 |  | Manual | Electronic
234 | Maintenance | Ground | Maintenance office 2 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 | 1 |  | Manual | Electronic
236 | Maintenance | Ground | Electric-ians' room 1 | Fl. | T12-4 | 4 | 2 | 1 | 2 | 40 | 80 | 9 | 9 | 5.04 | 2 |  | Manual | Magnetic
229 | Maintenance | Ground | Maintenance office 1 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 12.5 | 12.5 | 3.5 | 1 |  | Manual | Magnetic
237 | Maintenance | Ground | Electric-ians' room 2 | Fl. | T12-4 | 4 | 3 | 1 | 3 | 40 | 120 | 9 | 9 | 7.56 | 2 |  | Manual | Magnetic
238 | Maintenance | Ground | Male bathroom | Fl. | T12-4 | 4 | 2 | 1 | 2 | 40 | 80 | 3 | 3 | 1.68 | 1 |  | Manual | Magnetic
239 | Maintenance | Ground | Female bathroom | Fl. | T12-4 | 4 | 2 | 1 | 2 | 40 | 80 | 4 | 4 | 2.24 | 1 |  | Manual | Magnetic
235 | Maintenance | Ground | Maintenance office 2 | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 | 8 | 1.12 | 1 |  | Manual | Electronic
241 | Medical Records | Ground | Reception Area | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
242 | Medical Records | Ground | Lobby | Fl. | T12-4 | 4 | 6 | 2 | 12 | 40 | 480 | 12 | 12 | 40.32 | 1
243 | Medical Records | Ground | File room 1 | Fl. | T12-4 | 4 | 6 | 2 | 12 | 40 | 480 | 2 |  | 4.8 | 1
244 | Medical Records | Ground | Store Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 2 |  | 0.8 | 1
245 | Medical Records | Ground | File Room 2 | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 2 |  | 2.4 | 1
246 | Medical Records | Ground | File Room 3 | Fl. | T12-4 | 4 | 6 | 2 | 12 | 40 | 480 | 2 |  | 4.8 | 1
247 | Medical Records | Ground | Bath Room 3 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
248 | Medical Records | Ground | Passage | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 | 12 | 13.44 | 1
249 | Nurses’ Quarters | Ground | Nurses’ Quarters/ | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 12 | 12 | 6.048 | 2
250 | Nurses’ Quarters | Ground | Office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 |  | 2.88 | 2
251 | Nurses’ Quarters | Ground | Living room/bathroom | Fl. | T12-4 | 4 | 2 | 2 | 4 | 36 | 144 | 12 | 12 | 12.096 | 1
252 | Nurses’ Quarters | Ground | Bedroom | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 4 | 4 | 2.016 | 1
253 | Nurses’ Quarters | Ground | Kitchen | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 | 1
254 | Nurses’ Quarters | Ground |  | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 | 1
255 | Nurses’ Quarters | Ground | Nurses office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 | 1
256 | Nurses’ Quarters | Ground | Dental office | Fl. | T12-4 | 4 | 1 | 1 | 1 | 36 | 36 | 8 | 8 | 2.016 | 1
263 | Occupational Therapy | Ground | Store room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 2 |  | 0.72 | 1
264 | Occupational Therapy | Ground | Veranda | Fl. | T12-4 | 4 | 4 | 2 | 8 | 36 | 288 | 12 |  | 17.28
265 | Occupational Therapy | Ground | Veranda | Fl. | T12-4 | 4 | 2 | 1 | 2 | 36 | 72 | 12 |  | 4.32
257 | Occupational Therapy | Ground | Manager | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 |  | 2.88 | 1
258 | Occupational Therapy | Ground | Pantry | Fl. | T12-4 | 4 | 3 | 2 | 6 | 36 | 216 | 8 |  | 8.64 | 1
260 | Occupational Therapy | Ground | TV room | Fl. | T12-4 | 4 | 5 | 1 | 5 | 36 | 180 | 8 |  | 7.2 | 1
262 | Occupational Therapy | Ground | Bathroom | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 22 | 4 | 4.72 | 1
259 | Occupational Therapy | Ground | Staff bathroom | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 8 |  | 3.2 | 1
261 | Occupational Therapy | Ground | Patient bathroom | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 |  | 0.8 | 1
269 | Perimeter Lighting | Pole Mount | Dust to Dawn Light | 175 SVL | X-Security | n/a | 55 | 1 | 55 | 175 | 9625 | 12 | 12 | 808.5
267 | Perimeter Lighting | Pole Mount | Perimeter Lighting | Solar Light | X-Security | n/a | 5 | 1 | 5 | 36 | 180 | 12 | 12 | n/a |  |  | Photo-cell
266 | Perimeter Lighting | Pole Mount | LED Perimeter Lighting | 250W HPS | X-Security | n/a | 25 | 1 | 25 | 250 | 6250 | 12 | 12 | 525 |  |  | Photo-cell
583 | Perimeter Lighting |  |  | 125W Spot | X-Security | n/a | 2 | 1 | 2 | 125 | 250 | 12 | 12 | 21
284 | Pharmacy | Ground | Room 3 | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 8 | 8 | 3.36
286 | Pharmacy | Ground | Passage | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 12 | 8 | 4.56
280 | Pharmacy | Ground | Vault | Incandescent | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 2 |  | 0.6
285 | Pharmacy | Ground | Passage | Incandescent | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 12 |  | 3.6
270 | Pharmacy | Ground | Office Cubicle | Fl. | T12-4 | 4 | 6 | 2 | 12 | 40 | 480 | 8 |  | 19.2 | 1
271 | Pharmacy | Ground | Room 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1
272 | Pharmacy | Ground | Room 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1
273 | Pharmacy | Ground | Director of Finance | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1
274 | Pharmacy | Ground | File Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 2 |  | 0.8 | 1
275 | Pharmacy | Ground | Registry | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1
276 | Pharmacy | Ground | Office | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 |  | 6.4 | 1
277 | Pharmacy | Ground | Passage | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 |  | 4.8 | 1
279 | Pharmacy | Ground | Vault | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 2 |  | 0.8 | 1
281 | Pharmacy | Ground | Accounting Clerk Data Entry | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1
278 | Pharmacy | Ground | Passage | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 |  | 2.4 | 1
282 | Pharmacy | Ground | Female Bath room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 | 1
283 | Pharmacy | Ground | Male Bath Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 | 1
290 | Rainbow Centre | Ground | Room 3 | Incandescent | Bulb | n/a | 2 | 1 | 2 | 60 | 120 | 8 |  | 4.8 | 1
291 | Rainbow Centre | Ground | Room 4 | Incandescent | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 8 |  | 2.4 | 1
288 | Rainbow Centre | Ground | Room 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1
289 | Rainbow Centre | Ground | Room 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1
292 | Rainbow Centre | Ground | Consulting Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
296 | Rainbow Centre | First | Passage | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72
298 | Rainbow Centre | First | Bath Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
299 | Rainbow Centre | First | Sleeping Area | Fl. | T12-4 | 4 | 10 | 2 | 20 | 40 | 800 | 4 | 4 | 22.4 | 1
301 | Rainbow Centre | First | Passage | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 | 1
303 | Rainbow Centre | First | Kitchen | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 | 1
293 | Rainbow Centre | Ground | Room 5 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 | 1
294 | Rainbow Centre | Ground | Bath Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 | 1
295 | Rainbow Centre | First | Passage | Fl. | T8-2 | 2 | 3 | 2 | 6 | 20 | 120 | 12 | 12 | 10.08 | 1
297 | Rainbow Centre | First | Staff Lounge | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 | 1
300 | Rainbow Centre | First | Sleeping Area | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 8 |  | 3.2 | 1
302 | Rainbow Centre | First | Passage | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36 | 1
304 | Rainbow Centre | First | Utility Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 |  | 0.4 | 1
305 | Rainbow Centre | First | Bath Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 | 1
306 | Rainbow Centre | First | Staircase | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36 | 1
309 | Recreational Area | Ground | Male Restroom | Fl. | T12-2 | 4 | 1 | 2 | 2 | 40 | 80 | 10 | 10 | 5.6 | 1 | 1 | Switch | Electronic Ballast
308 | Recreational Area | Ground | Main Hall | Fl. | T12-4 | 4 | 12 | 2 | 24 | 40 | 960 | 10 | 10 | 67.2 | 1 | 1 | Switch | Electronic Ballast
310 | Recreational Area | Ground | Female Restroom | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | Not used | Not used |  | 1 | 1 | Switch | Electronic Ballast
311 | Recreational Area | Ground | Store Room | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | Not used | Not used |  | 1 | 1 | Switch | Electronic Ballast
315 | Rehad Ward | Ground | Corridor | Fl. | Bulb | n/a | 2 | 1 | 2 | 40 | 80 | 12 | 12 | 6.72
324 | Rehad Ward | Ground | Bath Room 2 | Fl. | Bulb | n/a | 2 | 1 | 2 | 40 | 80 | 8 | 8 | 4.48
313 | Rehad Ward | Ground | Eating Area | Fl. | T12-4 | 4 | 8 | 2 | 16 | 40 | 640 | 8 | 8 | 35.84
314 | Rehad Ward | Ground | Corridor | Fl. | T12-4 | 4 | 10 | 2 | 20 | 40 | 800 | 12 | 12 | 67.2
317 | Rehad Ward | Ground | Room 1 - 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48
320 | Rehad Ward | Ground | Room 9 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24
325 | Rehad Ward | Ground | Nurse Station | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 8 | 8 | 17.92
327 | Rehad Ward | Ground | Room 21 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48
316 | Rehad Ward | Ground | Bath Room 1 | Fl. | T8-2 | 2 | 2 | 1 | 2 | 20 | 40 | 8 | 8 | 2.24
318 | Rehad Ward | Ground | Room 3,4,5,6,8 & 10 | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 | 8 | 1.12
319 | Rehad Ward | Ground | Room7 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6
321 | Rehad Ward | Ground | Room 12,15,16,18,19 | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 |  | 0.8
322 | Rehad Ward | Ground | Room 11,13,14,17,20 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6
323 | Rehad Ward | Ground | Bath Room 2 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24
326 | Rehad Ward | Ground | Bath Room 3 | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 | 8 | 1.12
328 | Rehad Ward | Ground | Room 22-25 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6
344 | Rock Ward | Ground | Corridor | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 12 | 12 | 5.04
331 | Rock Ward | Ground | Room 1-2 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 36 | 144 | 8 | 8 | 8.064 | 1
333 | Rock Ward | Ground | Patient bath Room | Fl. | T12-4 | 4 | 2 | 2 | 4 | 36 | 144 | 8 | 8 | 8.064 | 1
334 | Rock Ward | Ground | Bathroom 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 | 1
335 | Rock Ward | Ground | Bathroom 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 | 1
340 | Rock Ward | Ground | Nurse Station/Pantry | Fl. | T12-4 | 4 | 4 | 1 | 4 | 36 | 144 | 12 | 12 | 12.096
343 | Rock Ward | Ground | Corridor | Fl. | T12-4 | 4 | 7 | 1 | 7 | 36 | 252 | 12 | 12 | 21.168 | 1
330 | Rock Ward | Ground | Staff Bath Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 | 1
332 | Rock Ward | Ground | Room 3-4- | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 | 1
336 | Rock Ward | Ground | Closet | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 2 |  | 0.2 | 1
337 | Rock Ward | Ground | Treatment Room | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 12 | 12 | 1.68
338 | Rock Ward | Ground | Room 5-10 | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 |  | 0.8
339 | Rock Ward | Ground | Visitors Room | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 | 8 | 1.12
341 | Rock Ward | Ground | Room 11-19 | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 | 8 | 1.12
346 | Sanitation | Ground | Sanitation super-visor | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 | 1
347 | Sanitation | Ground | Trans-portation room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
348 | Sanitation | Ground | Trans-portation super-visor | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 8 | 8 | 17.92 | 1
352 | Sanitation | Ground | House-keeping super-visor | Fl. | T12-4 | 4 | 2 | 1 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
353 | Sanitation | Ground | Room 1 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 |  | 1.6 | 1
354 | Sanitation | Ground | Room 2 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 |  | 1.6 | 1
358 | Sanitation | Ground | Ground staff room | Fl. | T12-4 | 4 | 6 | 2 | 12 | 40 | 480 | 8 |  | 19.2 | 1
349 | Sanitation | Ground | Bath Room 1 | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 8 | 8 | 4.48 | 1
350 | Sanitation | Ground | Passage | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36 | 1
351 | Sanitation | Ground | Passage | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 12 | 12 | 1.68
355 | Sanitation | Ground | Bathroom (m) | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1
356 | Sanitation | Ground | Bathroom (f) | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1
357 | Sanitation | Ground | Sanitation bathroom | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1
359 | Sanitation | Ground | Passage | Fl. | T8-2 | 2 | 5 | 1 | 5 | 20 | 100 | 12 | 12 | 8.4 | 1
362 | Security House | Ground | Locker room | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 2 | 2 | 0.84 | 1
361 | Security House | Ground | Female Patients bathroom | Incandescent | Bulb | n/a | 2 | 1 | 2 | 60 | 120 | 8 | 8 | 6.72 | 1
364 | Security House | Ground | Male Patients bathroom | Incandescent | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 8 | 8 | 3.36
363 | Security House | Ground | Security Post | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36 | 1
374 | Social Work | Ground | Lobby area (rear) | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 12 |  | 3.6
366 | Social Work | Ground | Senior Social work office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1
367 | Social Work | Ground | Social work office 1 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 |  | 6.4 | 4
369 | Social Work | Ground | Kitchen/ | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 |  | 4.8 | 1
370 | Social Work | Ground | Pantry area | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 2 |  | 0.8 | 1
371 | Social Work | Ground | Staff bathroom | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1
372 | Social Work | Ground | Social work office 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 2
373 | Social Work | Ground | Lobby area (rear) | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 |  | 9.6 | 3
368 | Social Work | Ground | Social work office 2 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6
375 | Social Work | Ground | Passage area | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 |  | 2.4 | 1
382 | Staff Cafeteria | Ground | Passage 2 | fl. | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 12 | 12 | 3.36 | 1
377 | Staff Cafeteria | Ground | Bath room 1 & 2 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 | 1
378 | Staff Cafeteria | Ground | Area 1 | Fl. | T12-4 | 4 | 5 | 2 | 10 | 40 | 400 | 8 | 8 | 22.4 | 1
380 | Staff Cafeteria | Ground | Lunch Room | Fl. | T12-4 | 4 | 5 | 2 | 10 | 40 | 400 | 8 | 8 | 22.4 | 1
381 | Staff Cafeteria | Ground | Passage 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 | 1
383 | Staff Cafeteria | Ground | Eating Area | Fl. | T12-4 | 4 | 5 | 2 | 10 | 40 | 400 | 10 | 10 | 28 | 1 | 1 | Switch | Electronic Ballast
385 | Staff Cafeteria | Ground | Store Room 3 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1 | 1 | Switch | Electronic Ballast
379 | Staff Cafeteria | Ground | Passage 1 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36 | 1
384 | Staff Cafeteria | Ground | Areaa 2 & 3 | Fl. | T8-2 | 2 | 6 | 2 | 12 | 20 | 240 | 12 | 12 | 20.16 | 1
386 | Staff Cafeteria | Ground | Store Room 2 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 10 | 10 | 2.8 | 1 | 1 | Switch | Electronic Ballast
387 | Staff Cafeteria | Ground | Store Room 1 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 10 | 10 | 2.8 | 1 | 1 | Switch | Electronic Ballast
403 | Ward 2 | Ground | Room 1,3,6,7,10,11,14,15 | Fl. | Bulb | n/a | 8 | 1 | 8 | 60 | 480 | 8 | 8 | 26.88 | 1
414 | Ward 2 | Ground | Sick Bay | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 8 | 8 | 3.36
416 | Ward 2 | Ground | Passage 1&2 | Fl. | Bulb | n/a | 2 | 1 | 2 | 60 | 120 | 12 | 12 | 10.08
402 | Ward 2 | Ground | Bath room 1 & 2 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 | 1
404 | Ward 2 | Ground | Room 2,4,5,8,9,12,13,16 | Fl. | T12-4 | 4 | 8 | 2 | 16 | 40 | 640 | 8 | 8 | 35.84 | 1
407 | Ward 2 | Ground | Treatment Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
408 | Ward 2 | Ground | Nurse Change Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
409 | Ward 2 | Ground | Nurse Station | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 | 12 | 13.44 | 1
411 | Ward 2 | Ground | Clothes Room | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 2 | 2 | 0.56 | 1
412 | Ward 2 | Ground | Area 3 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1
413 | Ward 2 | Ground | Area 4 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 | 1
415 | Ward 2 | Ground | Eating Area | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 | 1
405 | Ward 2 | Ground | Area 1 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1
406 | Ward 2 | Ground | Area 2 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1
410 | Ward 2 | Ground | Nurse Station | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 8 | 8 | 4.48
419 | Ward 3 | Ground | Clothes Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
420 | Ward 3 | Ground | Sick Bay | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
423 | Ward 3 | Ground | Room 8, 12 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 | 1
424 | Ward 3 | Ground | Nurse Station | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 | 12 | 13.44 | 1
425 | Ward 3 | Ground | Treatment Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
426 | Ward 3 | Ground | Lunch Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
427 | Ward 3 | Ground | Office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
433 | Ward 3 | Ground | Passage 3 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72
418 | Ward 3 | Ground | Area 1 | Fl. | T8-2 | 2 | 3 | 1 | 3 | 20 | 60 | 8 | 8 | 3.36 | 1
421 | Ward 3 | Ground | Room 1, 3, 4,5,7,9,13,11,12,15 | Fl. | T8-2 | 2 | 10 | 1 | 10 | 20 | 200 | 8 | 8 | 11.2 | 1
422 | Ward 3 | Ground | Room 2,6,1014 | Fl. | T8-2 | 2 | 4 | 2 | 8 | 20 | 160 | 8 | 8 | 8.96 | 1
428 | Ward 3 | Ground | Room 16 | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 | 8 | 1.12 | 1
429 | Ward 3 | Ground | Passage 1 | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 12 | 12 | 6.72 | 1
430 | Ward 3 | Ground | Passage 2 | Fl. | T8-2 | 2 | 2 | 1 | 2 | 20 | 40 | 12 | 12 | 3.36
431 | Ward 3 | Ground | Passage 2 | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 12 | 12 | 1.68 | 1
432 | Ward 3 | Ground | Passage 3 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36
434 | Ward 3 | Ground | Passage 3 | Fl. | T8-2 | 2 | 2 | 1 | 2 | 20 | 40 | 12 | 12 | 3.36
435 | Ward 3 | Ground | Room 17 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1
436 | Ward 3 | Ground | Room 18 | fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24
455 | Ward 4 or little G | Ground | Room 1, 8, 10 & 14 | Incandescent | Bulb | n/a | 4 | 1 | 4 | 40 | 160 | 8 | 8 | 8.96
441 | Ward 4 or little G | Ground | Passage | Incandescent | Bulb | n/a | 2 | 1 | 2 | 40 | 80 | 12 | 12 | 6.72 | 1
442 | Ward 4 or little G | Ground | Room 2, 4, 7, 9, 11, 13, 15 & 16 | Incandescent | Bulb | n/a | 8 | 1 | 8 | 40 | 320 | 8 | 8 | 17.92 | 1
443 | Ward 4 or little G | Ground | Room 5 | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 20 | 8 | 8 | 1.12 | 1
440 | Ward 4 or little G | Ground | Passage | Fl. | T12-4 | 4 | 5 | 1 | 5 | 40 | 200 | 12 | 12 | 16.8 | 1
444 | Ward 4 or little G | Ground | Room 10 & 14 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 | 1
445 | Ward 4 or little G | Ground | Room 6 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 | 1
446 | Ward 4 or little G | Ground | Room 18 | Fl. | T12-4 | 4 | 6 | 2 | 12 | 40 | 480 | 8 | 8 | 26.88 | 1
447 | Ward 4 or little G | Ground | Area 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
448 | Ward 4 or little G | Ground | Treatment Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48
449 | Ward 4 or little G | Ground | Room 3, 12 & 17 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
450 | Ward 4 or little G | Ground | Bath Room 1-4 | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 8 | 8 | 17.92 | 1
451 | Ward 4 or little G | Ground | Lunch Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
452 | Ward 4 or little G | Ground | Area 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
453 | Ward 4 or little G | Ground | Closet | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 2 | 2 | 0.56
454 | Ward 4 or little G | Ground | Closet | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 2 | 2 | 1.12
479 | Ward 5 | Ground | Room 9 | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 | 1
480 | Ward 5 | Ground | Room 13 | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24
477 | Ward 5 | Ground | Passage | Incandescent | Bulb | n/a | 2 | 1 | 2 | 40 | 80 | 12 | 12 | 6.72
457 | Ward 5 | Ground | Room 1 | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 | 1
460 | Ward 5 | Ground | Room 4 | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 | 1
462 | Ward 5 | Ground | Room 5 | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 | 1
465 | Ward 5 | Ground | Room 8 | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 | 1
474 | Ward 5 | Ground | Room10 & 14 | Incandescent | Bulb | n/a | 2 | 1 | 2 | 40 | 80 | 8 | 8 | 4.48
476 | Ward 5 | Ground | Room 12 & 17 | Incandescent | Bulb | n/a | 2 | 1 | 2 | 40 | 80 | 8 | 8 | 4.48
461 | Ward 5 | Ground | Room 19 | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 20 | 8 | 8 | 1.12 | 1
478 | Ward 5 | Ground | Passage | Fl. | T12-2 | 4' | 5 | 2 | 10 | 40 | 400 | 12 | 12 | 33.6
456 | Ward 5 | Ground | Bath Room 1 - 4 | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 8 | 8 | 17.92 | 1
458 | Ward 5 | Ground | Room 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
459 | Ward 5 | Ground | Room 3 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
463 | Ward 5 | Ground | Room 6 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
464 | Ward 5 | Ground | Room 7 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 | 1
466 | Ward 5 | Ground | Room 9 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
467 | Ward 5 | Ground | Room 18 | Fl. | T12-4 | 4 | 6 | 2 | 12 | 40 | 480 | 8 | 8 | 26.88 | 1
468 | Ward 5 | Ground | Area 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
469 | Ward 5 | Ground | Area 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
470 | Ward 5 | Ground | Treatment Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
471 | Ward 5 | Ground | Lunch Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
472 | Ward 5 | Ground | Sisters Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
473 | Ward 5 | Ground | Room 13 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
475 | Ward 5 | Ground | Room 11, 15 & 16 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
484 | Ward 6 | Ground | Lunch Room | Fl. | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 | 1
486 | Ward 6 | Ground | Bath Room4 | Fl. | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24
488 | Ward 6 | Ground | Room 1,8,10,13 | Fl. | Bulb | n/a | 4 | 1 | 4 | 40 | 160 | 8 | 8 | 8.96
501 | Ward 6 | Ground | Passage 1 | Fl. | Bulb | n/a | 2 | 1 | 2 | 40 | 80 | 8 | 8 | 4.48
490 | Ward 6 | Ground | Room 9,12 | Fl. | Bulb | n/a | 2 | 1 | 2 | 40 | 80 | 8 | 8 | 4.48
483 | Ward 6 | Ground | Bath Room 5 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
485 | Ward 6 | Ground | Bath Room3 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48
489 | Ward 6 | Ground | Room 9,12 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 | 1
491 | Ward 6 | Ground | Nurse Station | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
492 | Ward 6 | Ground | Treatment Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
493 | Ward 6 | Ground | Lunch Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
494 | Ward 6 | Ground | Sister’s Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
495 | Ward 6 | Ground | Passage 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 | 1
496 | Ward 6 | Ground | Room 16 & 17 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96
497 | Ward 6 | Ground | Bath Room 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48
498 | Ward 6 | Ground | Bath Room 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48
499 | Ward 6 | Ground | Room 7 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24
500 | Ward 6 | Ground | Passage 1 | Fl. | T12-4 | 4 | 2 | 1 | 2 | 40 | 80 | 12 | 12 | 6.72
487 | Ward 6 | Ground | Room 2,3,4,5,6,11, 14 | Fl. | T12-4 | 4 | 7 | 2 | 14 | 40 | 560 | 8 | 8 | 31.36 | 1
482 | Ward 6 | Ground | Room 15 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1
506 | Ward K / K Complex | Ground | Passage 1 | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 12 | 12 | 5.04
504 | Ward K / K Complex | Ground | Passage 1 | Fl. | T12-4 | 4 | 5 | 2 | 10 | 40 | 400 | 12 | 12 | 33.6
507 | Ward K / K Complex | Ground | Sleeping area | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 6 | 6 | 13.44 | 2 |  | Manual | Magnetic
508 | Ward K / K Complex | Ground | Bath Room 1 | Fl. | T12-4 | 4 | 2 | 1 | 2 | 40 | 80 | 6 | 6 | 3.36 | 2 |  | Manual | Magnetic
509 | Ward K / K Complex | Ground | Staff bathroom | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 4 | 4 | 2.24 | 1 |  | Manual | Magnetic
510 | Ward K / K Complex | Ground | Pantry | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 4 | 4 | 2.24 | 1 |  | Manual | Magnetic
511 | Ward K / K Complex | Ground | utility room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 4 | 4 | 2.24 | 1 |  | Manual | Magnetic
512 | Ward K / K Complex | Ground | Kitchen | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 5 | 5 | 5.6 | 1 |  | Manual | Magnetic
513 | Ward K / K Complex | Ground | Area 1 | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 5 | 5 | 8.4 | 1 |  | Manual | Magnetic
514 | Ward K / K Complex | Ground | Passage 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 5 | 5 | 2.8 | 1 |  | Manual | Magnetic
515 | Ward K / K Complex | Ground | Bath Room 2 | Fl. | T12-4 | 4 | 2 | 1 | 2 | 40 | 80 | 6 | 6 | 3.36 | 1 |  | Manual | Magnetic
503 | Ward K / K Complex | Ground | Room 1 | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 20 | 8 | 8 | 1.12
505 | Ward K / K Complex | Ground | Passage 1 | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 20 | 12 | 12 | 1.68
516 | Ward K / K Complex | Ground | Room 1 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 20 | 6 | 6 | 0.84 | 1 |  | Manual | Magnetic
548 | Ward Lower C | Ground | Isolating Room | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24
544 | Ward Lower C | Ground | Lobby | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 | 1 |  | Manual | Magnetic
545 | Ward Lower C | Ground | Bath Room 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
546 | Ward Lower C | Ground | Eating area | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 | 1
547 | Ward Lower C | Ground | Isolating Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1
549 | Ward Lower C | Ground | Patient Area 1 | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 8 | 8 | 13.44 | 1
550 | Ward Lower C | Ground | Patient Area 2 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 | 1
552 | Ward Lower C | Ground | Patient Area 3 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96
553 | Ward Lower C | Ground | Room 1 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 | 1
554 | Ward Lower C | Ground | Room 2 | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 8 | 8 | 13.44 | 1
555 | Ward Lower C | Ground | Staff Area | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 | 12 | 13.44 | 2 |  | Manual | Magnetic
556 | Ward Lower C | Ground | Staff Area | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 | 12 | 13.44 | 2 |  | Manual | Magnetic
551 | Ward Lower C | Ground | Patient Area 3 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24
543 | Ward Upper C | First | Staff Room 2 | FL. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 8 | 8 | 3.36
559 | Ward Upper C | First | Staff Room 1 & 3 | Incandescent | Bulb | n/a | 2 | 1 | 2 | 60 | 120 | 4 | 4 | 3.36 |  |  | Manual | Magnetic
524 | Ward Upper C | First | Nurses' station | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 | 2 |  | Manual | Magnetic
525 | Ward Upper C | First | Nurses' station | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 12 | 12 | 3.36
530 | Ward Upper C | First | Treatment room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 5 | 5 | 1.4 | 1 |  | Manual | Magnetic
526 | Ward Upper C | First | Water Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 20 | 8 | 8 | 1.12
527 | Ward Upper C | First | Changing Area | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 20 | 8 | 8 | 1.12
529 | Ward Upper C | First | Eating Area | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 6 | 6 | 1.68 |  |  | Manual | Magnetic
531 | Ward Upper C | First | Bathroom 1 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 6 | 6 | 1.68 | 1 |  | Manual | Magnetic
532 | Ward Upper C | First | Bathroom 2 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 6 | 6 | 1.68 | 1 |  | Manual | Magnetic
533 | Ward Upper C | First | Corridor | Fl. | T8-2 | 2 | 6 | 1 | 6 | 20 | 120 | 6 | 6 | 5.04 | 1 |  | Manual | Magnetic
534 | Ward Upper C | First | Room 1-17 | Fl. | T8-2 | 2 | 17 | 2 | 34 | 20 | 680 | 6 | 6 | 28.56 | 1 |  | Manual | Magnetic
561 | Ward Villa 1 | Ground | Dormitory | Fl. | T12-4 | 4 | 6 | 2 | 12 | 40 | 480 | 5 | 5 | 16.8 | 1 |  | Switch | Electronic Ballast
562 | Ward Villa 1 | Ground | Bath Room | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 | 1 |  | Switch | Electronic Ballast
567 | Ward Villa 1 | Ground | Main Corridor | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 12 | 12 | 20.16 | 1 |  | Switch | Electronic Ballast
564 | Ward Villa 1 | Ground | Nurses Lunch | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96
568 | Ward Villa 1 | Ground | Staff Area | LED | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 | 1 |  | Switch
563 | Ward Villa 1 | Ground | Nurses lunch area | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1 |  | Switch | Electronic Ballast
565 | Ward Villa 1 | Ground | Nurses Rest Area | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1 |  | Switch | Electronic Ballast
566 | Ward Villa 1 | Ground | Wsh Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1
571 | Ward Villa 2 | Ground | Dormitory | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 | 1 | 1 | Switch | Electronic Ballast
573 | Ward Villa 2 | Ground | Dormitory | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 |  | 2 | Switch | Electronic Ballast
574 | Ward Villa 2 | Ground | Clothes Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 4 |  | 1.6 | 1 | 1 | Switch | Electronic Ballast
575 | Ward Villa 2 | Ground | Passage 1&2 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 | 12 | 13.44 | 1 | 1 | Switch | Electronic Ballast
578 | Ward Villa 2 | Ground | Main Corridor | Fl. | T12-4 | 4 | 5 | 2 | 10 | 40 | 400 | 12 | 12 | 33.6 | 1 |  | Switch | Electronic Ballast
570 | Ward Villa 2 | Ground | Nurses Station | Fl. | T12-4 | 4 | 7 | 2 | 14 | 40 | 560 | 12 | 12 | 47.04 | 1 | 1 | Switch
572 | Ward Villa 2 | Ground | Dormitory | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 8 | 8 | 4.48 | 1 | 1 | Switch | Electronic Ballast
576 | Ward Villa 2 | Ground | Staff Rest Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 4 | 4 | 1.12 | 1 | 1 | Switch
577 | Ward Villa 2 | Ground | Security Post | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36 | 1 | 1 | Switch
579 | Ward Villa 2 | Ground | Patients Bathroom | LED | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 | 1 | 1 | Switch

## Lighting Details BVH 26Apr19
Ref # | Zone | Floor Name / Number | Room Name/ Number | Equipment Type (LED, Fluorescent, incandescent) | Tube Type (T5, T8, etc) | Fixture Length | # of Fixtures | Tubes per Fixture | No of Tubes/ bulbs | Power /bulb-tube (W) | Inst'lld Power (W) | Week day usage, Hrs/day | Weekend usage, hrs/day | Total Usage kWHrs/Week |  | # of switches in room | Number of switches per fixture | Control Type | Ballast Type (Electronic, Magnetic)
3 | Admin Building | Ground | Females Bathroom | Fl. | Bulb | n/a | 1 | 1 | 1 | 100 | 100 | 4 | 4 | 2.8 |  | 1 | 1 | Switch | Electronic
2 | Admin Building | Ground | Corridor | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 12 | 12 | 5.04 |  | 1
57 | B Ward | First | Staff bathroom | Incandescent | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 2 | 2 | 0.84 |  | 1
60 | B Ward | First | Chemical room | Fl. | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 |  | 1.6 |  | 1
61 | B Ward | First | Staff room 2 | Fl. | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 |  | 1
65 | B Ward | First | Treatment room | Fl. | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 12 | 12 | 3.36 |  | 1
69 | B Ward | First | Loiter room | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 |  | 1
70 | B Ward | First | Staff room 1 | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 12 | 8 | 3.04 |  | 1
59 | B Ward | First | Store room | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 2 | 2 | 0.56 |  | 1
78 | Bougain-villea | Ground | Examin-ation room | Fl. | bulb | n/a | 1 | 1 | 1 | 60 | 60 | 12 | 12 | 5.04 |  | 1
79 | Bougain-villea | Ground | Room 9 - 13 | Fl. | bulb | n/a | 1 | 1 | 1 | 60 | 60 | 8 | 8 | 3.36 |  | 1
80 | Bougain-villea | Ground | Room 1-2 | Fl. | bulb | n/a | 1 | 1 | 1 | 60 | 60 | 8 | 8 | 3.36 |  | 1
209 | In-service education 1 | Ground | Confer-ence room bathroom | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 3 |  | 0.9 |  | 1 |  | Manual | Magnetic
193 | In-service education 2 | Ground | Library | Bulb | Bulb | n/a | 4 | 1 | 4 | 60 | 240 | 8 |  | 9.6 |  | 1
194 | In-service education 2 | Ground | Office | Fl. | Bulb | n/a | 3 | 1 | 3 | 60 | 180 | 6 |  | 5.4 |  | 3 |  | Manual | Electronic
195 | In-service education 2 | Ground | Lecture Room | Fl. | Bulb | n/a | 2 | 1 | 2 | 60 | 120 | 4 |  | 2.4 |  | 1 |  | Manual | Electronic
196 | In-service education 2 | Ground | room | Fl. | Bulb | n/a | 2 | 1 | 2 | 60 | 120 | 4 |  | 2.4 |  | 1 |  | Manual | Electronic
199 | In-service education 2 | Ground | Kitchen | Fl. | Bulb | n/a | 2 | 1 | 2 | 60 | 120 | 4 |  | 2.4 |  | 1 |  | Manual | Electronic
284 | Pharmacy | Ground | Room 3 | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 8 | 8 | 3.36
286 | Pharmacy | Ground | Passage | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 12 | 8 | 4.56
280 | Pharmacy | Ground | Vault | Incandescent | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 2 |  | 0.6
285 | Pharmacy | Ground | Passage | Incandescent | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 12 |  | 3.6
315 | Rehad Ward | Ground | Corridor | Fl. | Bulb | n/a | 2 | 1 | 2 | 40 | 80 | 12 | 12 | 6.72
344 | Rock Ward | Ground | Corridor | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 12 | 12 | 5.04
362 | Security House | Ground | Locker room | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 2 | 2 | 0.84 |  | 1
361 | Security House | Ground | Female Patients bathroom | Incandescent | Bulb | n/a | 2 | 1 | 2 | 60 | 120 | 8 | 8 | 6.72 |  | 1
364 | Security House | Ground | Male Patients bathroom | Incandescent | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 8 | 8 | 3.36
374 | Social Work | Ground | Lobby area (rear) | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 12 |  | 3.6
382 | Staff Cafeteria | Ground | Passage 2 | fl. | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 12 | 12 | 3.36 |  | 1
403 | Ward 2 | Ground | Room 1,3,6,7,10,11,14,15 | Fl. | Bulb | n/a | 8 | 1 | 8 | 60 | 480 | 8 | 8 | 26.88 |  | 1
414 | Ward 2 | Ground | Sick Bay | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 8 | 8 | 3.36
416 | Ward 2 | Ground | Passage 1&2 | Fl. | Bulb | n/a | 2 | 1 | 2 | 60 | 120 | 12 | 12 | 10.08
455 | Ward 4 or little G | Ground | Room 1, 8, 10 & 14 | Incandescent | Bulb | n/a | 4 | 1 | 4 | 40 | 160 | 8 | 8 | 8.96
479 | Ward 5 | Ground | Room 9 | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 |  | 1
480 | Ward 5 | Ground | Room 13 | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24
477 | Ward 5 | Ground | Passage | Incandescent | Bulb | n/a | 2 | 1 | 2 | 40 | 80 | 12 | 12 | 6.72
484 | Ward 6 | Ground | Lunch Room | Fl. | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 |  | 1
486 | Ward 6 | Ground | Bath Room4 | Fl. | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24
488 | Ward 6 | Ground | Room 1,8,10,13 | Fl. | Bulb | n/a | 4 | 1 | 4 | 40 | 160 | 8 | 8 | 8.96
501 | Ward 6 | Ground | Passage 1 | Fl. | Bulb | n/a | 2 | 1 | 2 | 40 | 80 | 8 | 8 | 4.48
506 | Ward K / K Complex | Ground | Passage 1 | Fl. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 12 | 12 | 5.04
543 | Ward Upper C | First | Staff Room 2 | FL. | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 8 | 8 | 3.36
559 | Ward Upper C | First | Staff Room 1 & 3 | Incandescent | Bulb | n/a | 2 | 1 | 2 | 60 | 120 | 4 | 4 | 3.36 |  |  |  | Manual | Magnetic
290 | Rainbow Centre | Ground | Room 3 | Incandescent | Bulb | n/a | 2 | 1 | 2 | 60 | 120 | 8 |  | 4.8 |  | 1
291 | Rainbow Centre | Ground | Room 4 | Incandescent | Bulb | n/a | 1 | 1 | 1 | 60 | 60 | 8 |  | 2.4 |  | 1
324 | Rehad Ward | Ground | Bath Room 2 | Fl. | Bulb | n/a | 2 | 1 | 2 | 40 | 80 | 8 | 8 | 4.48
441 | Ward 4 or little G | Ground | Passage | Incandescent | Bulb | n/a | 2 | 1 | 2 | 40 | 80 | 12 | 12 | 6.72 |  | 1
442 | Ward 4 or little G | Ground | Room 2, 4, 7, 9, 11, 13, 15 & 16 | Incandescent | Bulb | n/a | 8 | 1 | 8 | 40 | 320 | 8 | 8 | 17.92 |  | 1
457 | Ward 5 | Ground | Room 1 | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 |  | 1
460 | Ward 5 | Ground | Room 4 | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 |  | 1
462 | Ward 5 | Ground | Room 5 | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 |  | 1
465 | Ward 5 | Ground | Room 8 | Incandescent | Bulb | n/a | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 |  | 1
474 | Ward 5 | Ground | Room10 & 14 | Incandescent | Bulb | n/a | 2 | 1 | 2 | 40 | 80 | 8 | 8 | 4.48
476 | Ward 5 | Ground | Room 12 & 17 | Incandescent | Bulb | n/a | 2 | 1 | 2 | 40 | 80 | 8 | 8 | 4.48
490 | Ward 6 | Ground | Room 9,12 | Fl. | Bulb | n/a | 2 | 1 | 2 | 40 | 80 | 8 | 8 | 4.48
[5 empty] | Bulb Total |  | 95 |  | 95 |  | 4800 |  |  | 247.22 |  |  |  |  | 0
8 | Admin Building | First | Corridor | Fl. | T12-2 | 2 | 6 | 2 | 12 | 20 | 240 | 3 | 3 | 5.04 |  | 1 | 1 | Switch | Electronic
26 | Admin Building | First | CEO Dining Room | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 |  | 1 | 1 | Switch | Magnetic
27 | Admin Building | First | Bathroom | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 |  | 1 | 1 | Switch | Magnetic
4 | Admin Building | Ground | Lobby Area | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 6 | 6 | 1.68 |  | 2 | 1 | Switch | Magnetic
7 | Admin Building | Ground | Corridor | Fl. | T12-2 | 2 | 4 | 2 | 8 | 20 | 160 | 3 | 3 | 3.36 |  | 2 | 1 | Switch | Electronic
17 | Admin Building | Ground | Males Bathroom | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 4 | 4 | 1.12 |  | 1 | 1 | Switch | Electronic
18 | Admin Building | Ground | Photo-copy Room | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 0 | 1.6 |  | 1 | 1 | Switch | Electronic
36 | Admin Building | Ground | Passage | Fl. | T12-2 | 2 | 2 | 2 | 4 | 20 | 80 | 12 |  | 4.8 |  | 1 |  | Switch | Electronic Ballast
44 | Admin Building | Ground | Male Bathroom | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 3 |  | 0.6 |  | 1 |  | Switch | Electronic Ballast
45 | Admin Building | Ground | Male Bathroom | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 3 |  | 0.6 |  | 1 |  | Switch | Electronic Ballast
46 | Admin Building | Ground | Female Bathroom | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 3 |  | 0.6 |  | 1 |  | Switch | Electronic Ballast
47 | Admin Building | Ground | Female Bathroom | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 3 |  | 0.6 |  | 1 |  | Switch | Electronic Ballast
54 | Admin Building | Ground | Nurses sign in office | Fl. | T12-2 | 4 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24
146 | Doctor's Lounge | Ground | Passage | Fl. | T12-2 | 2 | 2 | 2 | 4 | 20 | 80 | 8 |  | 3.2 |  | 1 |  | Switch | Electronic Ballast
309 | Recreational Area | Ground | Male Restroom | Fl. | T12-2 | 4 | 1 | 2 | 2 | 40 | 80 | 10 | 10 | 5.6 |  | 1 | 1 | Switch | Electronic Ballast
443 | Ward 4 or little G | Ground | Room 5 | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 20 | 8 | 8 | 1.12 |  | 1
461 | Ward 5 | Ground | Room 19 | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 20 | 8 | 8 | 1.12 |  | 1
478 | Ward 5 | Ground | Passage | Fl. | T12-2 | 4' | 5 | 2 | 10 | 40 | 400 | 12 | 12 | 33.6
548 | Ward Lower C | Ground | Isolating Room | Fl. | T12-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24
[5 empty] | T12-2 Total |  | 33 |  | 66 |  | 1520 |  |  | 70.24 |  |  |  |  | 0
37 | Admin Building | Ground | Passage | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 |  | 9.6 |  | 1 |  | Switch | Electronic Ballast
105 | Day clinic | Ground | Room 1 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 |  | 6.4 |  | 1
208 | In-service education 1 | Ground | Pharmacy bathroom | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 3 |  | 1.2 |  | 1 |  | Manual | Magnetic
198 | In-service education 1 | Ground | room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 4 |  | 1.6 |  | 1 |  | Manual | Electronic
19 | Admin Building | First | Oper-ations Officer 1 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 3 | 0 | 2.4 |  | 1 | 1 | Switch | Magnetic
21 | Admin Building | First | Senior Medical Officer Secretary | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 0 | 3.2 |  | 1 | 1 | Switch | Electronic
22 | Admin Building | First | Senior Medical Officer | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 0 | 3.2 |  | 1 | 1 | Switch | Electronic
23 | Admin Building | First | Chief Executive Officer | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 0 | 6.4 |  | 1 | 1 | Switch | Magnetic
24 | Admin Building | First | Hospital Admin Secretary | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 0 | 3.2 |  | 2 | 1 | Switch | Magnetic
25 | Admin Building | First | Hospital Admin Office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 3 | 0 | 1.2 |  |  | 1 | Switch | Electronic
6 | Admin Building | Ground | Reception Area | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 24 | 24 | 26.88 |  | 2 | 1 | Switch | Electronic
9 | Admin Building | Ground | Director of Nursing Services Secretary | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 0 | 3.2 |  | 1 | 1 | Switch | Magnetic
10 | Admin Building | Ground | Director of Nursing Services Secretary | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 0 | 1.6 |  | 1 | 1 | Switch | Electronic
11 | Admin Building | Ground | Director of Nursing Services | Fl. | T12-4 | 4 | 2 | 1 | 2 | 40 | 80 | 8 | 0 | 3.2 |  | 1 | 1 | Switch | Magnetic
12 | Admin Building | Ground | Director of Nursing Services Lunch Room | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 0 | 1.6 |  | 1 | 1 | Switch | Magnetic
13 | Admin Building | Ground | Deputy Director of Nursing Services | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 0 | 3.2 |  | 1 | 1 | Switch | Electronic
14 | Admin Building | Ground | Deputy Director of Nursing Services | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 0 | 3.2 |  | 1 | 1 | Switch | Magnetic
15 | Admin Building | Ground | Human Resource Depart-ment | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 8 | 0 | 12.8 |  | 1 | 1 | Switch | Electronic
16 | Admin Building | Ground | Human Resource Manager | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 0 | 3.2 |  | 1 | 1 | Switch | Electronic
28 | Admin Building | Ground | Accounts Depart-ment | Fl. | T12-4 | 4 | 5 | 2 | 10 | 40 | 400 | 11 |  | 22 |  | 1 |  | Switch | Electronic Ballast
30 | Admin Building | Ground | Director Of Finance Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 11 |  | 4.4 |  | 1 |  | Switch | Electronic Ballast
31 | Admin Building | Ground | Director Of Finance Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 11 |  | 4.4 |  | 1 |  | Switch | Electronic Ballast
32 | Admin Building | Ground | Salary Super-visor's Office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 11 |  | 4.4 |  | 1 |  | Switch | Electronic Ballast
33 | Admin Building | Ground | Salary Super-visor's Office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 11 |  | 4.4 |  | 1 |  | Switch | Electronic Ballast
34 | Admin Building | Ground | Computer Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 4 | 5.44 |  | 1 |  | Switch | Electronic Ballast
35 | Admin Building | Ground | Computer Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 4 | 5.44 |  | 1 |  | Switch | Electronic Ballast
38 | Admin Building | Ground | Passage | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 |  | 4.8 |  | 1 |  | Switch | Electronic Ballast
42 | Admin Building | Ground | Registry Room | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 3 |  | 3.6 |  | 1 |  | Switch | Electronic Ballast
43 | Admin Building | Ground | Registry Room | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 3 |  | 3.6 |  | 1 |  | Switch | Electronic Ballast
48 | Admin Building | Ground | Cashier Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 11 |  | 4.4 |  | 1 |  | Switch | Electronic Ballast
86 | Bougain-villea | Ground | Bath Room 1 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 36 | 36 | 8 | 8 | 2.016 |  | 2
93 | Bougain-villea | Ground | Bathroom 3 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 36 | 36 | 8 | 8 | 2.016 |  | 1
88 | Bougain-villea | Ground | Bath Room 4 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 36 | 36 | 8 | 8 | 2.016 |  | 2
94 | Bougain-villea | Ground | Lobby | Fl. | T12-4 | 4 | 3 | 2 | 6 | 36 | 216 | 12 | 12 | 18.144 |  | 1
81 | Bougain-villea | Ground | Patients Bath Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 |  | 1
82 | Bougain-villea | Ground | Clothes room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 2 | 2 | 1.008 |  | 1
83 | Bougain-villea | Ground | Nurse Station | Fl. | T12-4 | 4 | 2 | 2 | 4 | 36 | 144 | 12 | 12 | 12.096 |  | 2
90 | Bougain-villea | Ground | Corridor | Fl. | T12-4 | 4 | 14 | 2 | 28 | 36 | 1008 | 12 | 12 | 84.672 |  | 1
95 | CSSD | Ground | CSSD office | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 0 | 6.4 |  | 1 |  | Manual | Magnetic
99 | Day clinic | Ground | Doctor's room 3 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 6 |  | 2.4 |  | 1 |  | Manual | Electronic
100 | Day clinic | Ground | Kitchen | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 |  | 4.8 |  | 1
106 | Day clinic | Ground | Doctor's room 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1 |  | Manual | Electronic
107 | Day clinic | Ground | Doctor's room 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1 |  | Manual | Electronic
110 | Day clinic | Ground | Doctors Room 4 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1
112 | Day clinic | Ground | Bath Room 1&3 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 |  | 6.4 |  | 1
101 | Day clinic | Ground | Kitchen | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 |  | 4.8 |  | 1
145 | Doctor's Lounge | Ground | Kitchen | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1 |  | Switch | Electronic Ballast
147 | Doctor's Lounge | Ground | Bathroom 1 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 |  | 1.6 |  | 1 |  | Switch | Electronic Ballast
148 | Doctor's Lounge | Ground | Room 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1 | 1 | Switch | Electronic Ballast
149 | Doctor's Lounge | Ground | Room 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1 | 1 | Switch | Electronic Ballast
150 | Doctor's Lounge | Ground | Lounge | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 |  | 6.4 |  | 1 | 1 | Switch | Electronic Ballast
153 | Eastern division office | Ground | Main office | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 8 | 8 | 13.44 |  | 1 |  | Manual | Magnetic
154 | Eastern division office | Ground | Bed Room 1-2 | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 8 | 8 | 13.44 |  | 2 |  | Manual | Magnetic
155 | Eastern division office | Ground | Bed Room 3 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 |  | 2 |  | Manual | Magnetic
156 | Eastern division office | Ground | Bathroom | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 |  | 1 |  | Manual | Magnetic
159 | Emergency Area | Ground | Bathroom | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1 | 1 | Switch | Electronic Ballast
160 | Emergency Area | Ground | Change Nurse Office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1 | 1 | Switch | Electronic Ballast
200 | In-service education 1 | Ground | Passage | Fl. | T12-4 | 4 | 1 | 2 | 2 | 39 | 78 | 8.5 |  | 3.315 |  | 1 |  | Manual | Electronic
201 | In-service education 1 | Ground | Patient services secretary's office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8.5 |  | 3.4 |  | 2 |  | Manual | Electronic
202 | In-service education 1 | Ground | Pharmacy | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 8 |  | 12.8 |  | 1 |  | Manual | Electronic
203 | In-service education 1 | Ground | Pharmacy kitchen | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 |  | 6.4 |  | 1 |  | Manual | Electronic
204 | In-service education 1 | Ground | Pharmacy store room | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 8 |  | 9.6 |  | 2 |  | Manual | Electronic
205 | In-service education 1 | Ground | Conference room | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 5 |  | 8 |  | 3 |  | Manual | Magnetic
206 | In-service education 1 | Ground | Confer-ence room back/ | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 1 |  | 1.6 |  | 1 |  | Manual | Magnetic
207 | In-service education 1 | Ground | storage | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 1 |  | 1.6 |  | 1 |  | Manual | Magnetic
210 | In-service education 1 | Ground | In-service bathroom | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 3 |  | 1.2 |  | 1 |  | Manual | Magnetic
215 | Laundry | Ground | Passage 2 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 | 12 | 13.44 |  | 1
217 | Laundry | Ground | Washing Area | Fl. | T12-4 | 4 | 12 | 2 | 24 | 40 | 960 | 8 | 8 | 53.76 |  | 1
219 | Laundry | Ground | Passage 3 | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 12 | 12 | 26.88 |  | 1
220 | Laundry | Ground | Room 2 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 |  | 1
221 | Laundry | Ground | Room 3 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 |  | 1
222 | Laundry | Ground | Office 1-3 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
223 | Laundry | Ground | Kitchen | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 |  | 1
225 | Maintenance | Ground | General store 1 -2 | Fl. | T12-4 | 4 | 8 | 1 | 8 | 40 | 320 | 12.5 | 12.5 | 28 |  | 2 |  | Manual | Magnetic
226 | Maintenance | Ground | General store 1 -2 | Fl. | T12-4 | 4 | 4 | 1 | 4 | 40 | 160 | 12.5 | 12.5 | 14 |  | 1 |  | Manual | Magnetic
227 | Maintenance | Ground | Bobber | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 12.5 | 12.5 | 3.5 |  | 1 |  | Manual | Magnetic
228 | Maintenance | Ground | Maintenance office 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12.5 | 12.5 | 7 |  | 1 |  | Manual | Magnetic
230 | Maintenance | Ground | work shop | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 8 | 8 | 17.92 |  | 1 |  | Manual | Electronic
231 | Maintenance | Ground | work shop | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 8 | 8 | 17.92 |  | 1 |  | Manual | Electronic
232 | Maintenance | Ground | Maintenance office 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1 |  | Manual | Electronic
233 | Maintenance | Ground | Maintenance office 1 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 |  | 1 |  | Manual | Electronic
234 | Maintenance | Ground | Maintenance office 2 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 |  | 1 |  | Manual | Electronic
236 | Maintenance | Ground | Electric-ians' room 1 | Fl. | T12-4 | 4 | 2 | 1 | 2 | 40 | 80 | 9 | 9 | 5.04 |  | 2 |  | Manual | Magnetic
241 | Medical Records | Ground | Reception Area | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
242 | Medical Records | Ground | Lobby | Fl. | T12-4 | 4 | 6 | 2 | 12 | 40 | 480 | 12 | 12 | 40.32 |  | 1
243 | Medical Records | Ground | File room 1 | Fl. | T12-4 | 4 | 6 | 2 | 12 | 40 | 480 | 2 |  | 4.8 |  | 1
244 | Medical Records | Ground | Store Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 2 |  | 0.8 |  | 1
245 | Medical Records | Ground | File Room 2 | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 2 |  | 2.4 |  | 1
246 | Medical Records | Ground | File Room 3 | Fl. | T12-4 | 4 | 6 | 2 | 12 | 40 | 480 | 2 |  | 4.8 |  | 1
247 | Medical Records | Ground | Bath Room 3 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
248 | Medical Records | Ground | Passage | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 | 12 | 13.44 |  | 1
249 | Nurses’ Quarters | Ground | Nurses’ Quarters/ | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 12 | 12 | 6.048 |  | 2
250 | Nurses’ Quarters | Ground | Office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 |  | 2.88 |  | 2
251 | Nurses’ Quarters | Ground | Living room/bathroom | Fl. | T12-4 | 4 | 2 | 2 | 4 | 36 | 144 | 12 | 12 | 12.096 |  | 1
252 | Nurses’ Quarters | Ground | Bedroom | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 4 | 4 | 2.016 |  | 1
253 | Nurses’ Quarters | Ground | Kitchen | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 |  | 1
254 | Nurses’ Quarters | Ground |  | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 |  | 1
255 | Nurses’ Quarters | Ground | Nurses office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 |  | 1
256 | Nurses’ Quarters | Ground | Dental office | Fl. | T12-4 | 4 | 1 | 1 | 1 | 36 | 36 | 8 | 8 | 2.016 |  | 1
263 | Occupational Therapy | Ground | Store room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 2 |  | 0.72 |  | 1
264 | Occupational Therapy | Ground | Veranda | Fl. | T12-4 | 4 | 4 | 2 | 8 | 36 | 288 | 12 |  | 17.28
265 | Occupational Therapy | Ground | Veranda | Fl. | T12-4 | 4 | 2 | 1 | 2 | 36 | 72 | 12 |  | 4.32
257 | Occupational Therapy | Ground | Manager | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 |  | 2.88 |  | 1
258 | Occupational Therapy | Ground | Pantry | Fl. | T12-4 | 4 | 3 | 2 | 6 | 36 | 216 | 8 |  | 8.64 |  | 1
260 | Occupational Therapy | Ground | TV room | Fl. | T12-4 | 4 | 5 | 1 | 5 | 36 | 180 | 8 |  | 7.2 |  | 1
308 | Recreational Area | Ground | Main Hall | Fl. | T12-4 | 4 | 12 | 2 | 24 | 40 | 960 | 10 | 10 | 67.2 |  | 1 | 1 | Switch | Electronic Ballast
310 | Recreational Area | Ground | Female Restroom | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | Not used | Not used |  |  | 1 | 1 | Switch | Electronic Ballast
311 | Recreational Area | Ground | Store Room | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | Not used | Not used |  |  | 1 | 1 | Switch | Electronic Ballast
313 | Rehad Ward | Ground | Eating Area | Fl. | T12-4 | 4 | 8 | 2 | 16 | 40 | 640 | 8 | 8 | 35.84
314 | Rehad Ward | Ground | Corridor | Fl. | T12-4 | 4 | 10 | 2 | 20 | 40 | 800 | 12 | 12 | 67.2
317 | Rehad Ward | Ground | Room 1 - 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48
320 | Rehad Ward | Ground | Room 9 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24
325 | Rehad Ward | Ground | Nurse Station | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 8 | 8 | 17.92
327 | Rehad Ward | Ground | Room 21 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48
331 | Rock Ward | Ground | Room 1-2 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 36 | 144 | 8 | 8 | 8.064 |  | 1
333 | Rock Ward | Ground | Patient bath Room | Fl. | T12-4 | 4 | 2 | 2 | 4 | 36 | 144 | 8 | 8 | 8.064 |  | 1
334 | Rock Ward | Ground | Bathroom 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 |  | 1
335 | Rock Ward | Ground | Bathroom 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 |  | 1
340 | Rock Ward | Ground | Nurse Station/Pantry | Fl. | T12-4 | 4 | 4 | 1 | 4 | 36 | 144 | 12 | 12 | 12.096
343 | Rock Ward | Ground | Corridor | Fl. | T12-4 | 4 | 7 | 1 | 7 | 36 | 252 | 12 | 12 | 21.168 |  | 1
377 | Staff Cafeteria | Ground | Bath room 1 & 2 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 |  | 1
378 | Staff Cafeteria | Ground | Area 1 | Fl. | T12-4 | 4 | 5 | 2 | 10 | 40 | 400 | 8 | 8 | 22.4 |  | 1
380 | Staff Cafeteria | Ground | Lunch Room | Fl. | T12-4 | 4 | 5 | 2 | 10 | 40 | 400 | 8 | 8 | 22.4 |  | 1
381 | Staff Cafeteria | Ground | Passage 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 |  | 1
383 | Staff Cafeteria | Ground | Eating Area | Fl. | T12-4 | 4 | 5 | 2 | 10 | 40 | 400 | 10 | 10 | 28 |  | 1 | 1 | Switch | Electronic Ballast
385 | Staff Cafeteria | Ground | Store Room 3 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1 | 1 | Switch | Electronic Ballast
440 | Ward 4 or little G | Ground | Passage | Fl. | T12-4 | 4 | 5 | 1 | 5 | 40 | 200 | 12 | 12 | 16.8 |  | 1
444 | Ward 4 or little G | Ground | Room 10 & 14 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 |  | 1
445 | Ward 4 or little G | Ground | Room 6 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 |  | 1
446 | Ward 4 or little G | Ground | Room 18 | Fl. | T12-4 | 4 | 6 | 2 | 12 | 40 | 480 | 8 | 8 | 26.88 |  | 1
447 | Ward 4 or little G | Ground | Area 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
448 | Ward 4 or little G | Ground | Treatment Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48
449 | Ward 4 or little G | Ground | Room 3, 12 & 17 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
450 | Ward 4 or little G | Ground | Bath Room 1-4 | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 8 | 8 | 17.92 |  | 1
451 | Ward 4 or little G | Ground | Lunch Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
452 | Ward 4 or little G | Ground | Area 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
453 | Ward 4 or little G | Ground | Closet | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 2 | 2 | 0.56
454 | Ward 4 or little G | Ground | Closet | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 2 | 2 | 1.12
456 | Ward 5 | Ground | Bath Room 1 - 4 | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 8 | 8 | 17.92 |  | 1
458 | Ward 5 | Ground | Room 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
459 | Ward 5 | Ground | Room 3 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
463 | Ward 5 | Ground | Room 6 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
464 | Ward 5 | Ground | Room 7 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24 |  | 1
466 | Ward 5 | Ground | Room 9 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
467 | Ward 5 | Ground | Room 18 | Fl. | T12-4 | 4 | 6 | 2 | 12 | 40 | 480 | 8 | 8 | 26.88 |  | 1
468 | Ward 5 | Ground | Area 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
469 | Ward 5 | Ground | Area 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
470 | Ward 5 | Ground | Treatment Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
471 | Ward 5 | Ground | Lunch Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
472 | Ward 5 | Ground | Sisters Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
473 | Ward 5 | Ground | Room 13 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
475 | Ward 5 | Ground | Room 11, 15 & 16 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
483 | Ward 6 | Ground | Bath Room 5 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
485 | Ward 6 | Ground | Bath Room3 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48
489 | Ward 6 | Ground | Room 9,12 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 |  | 1
491 | Ward 6 | Ground | Nurse Station | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
492 | Ward 6 | Ground | Treatment Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
493 | Ward 6 | Ground | Lunch Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
494 | Ward 6 | Ground | Sister’s Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
495 | Ward 6 | Ground | Passage 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 |  | 1
496 | Ward 6 | Ground | Room 16 & 17 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96
497 | Ward 6 | Ground | Bath Room 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48
498 | Ward 6 | Ground | Bath Room 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48
499 | Ward 6 | Ground | Room 7 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 | 8 | 2.24
500 | Ward 6 | Ground | Passage 1 | Fl. | T12-4 | 4 | 2 | 1 | 2 | 40 | 80 | 12 | 12 | 6.72
487 | Ward 6 | Ground | Room 2,3,4,5,6,11, 14 | Fl. | T12-4 | 4 | 7 | 2 | 14 | 40 | 560 | 8 | 8 | 31.36 |  | 1
504 | Ward K / K Complex | Ground | Passage 1 | Fl. | T12-4 | 4 | 5 | 2 | 10 | 40 | 400 | 12 | 12 | 33.6
507 | Ward K / K Complex | Ground | Sleeping area | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 6 | 6 | 13.44 |  | 2 |  | Manual | Magnetic
508 | Ward K / K Complex | Ground | Bath Room 1 | Fl. | T12-4 | 4 | 2 | 1 | 2 | 40 | 80 | 6 | 6 | 3.36 |  | 2 |  | Manual | Magnetic
509 | Ward K / K Complex | Ground | Staff bathroom | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 4 | 4 | 2.24 |  | 1 |  | Manual | Magnetic
510 | Ward K / K Complex | Ground | Pantry | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 4 | 4 | 2.24 |  | 1 |  | Manual | Magnetic
511 | Ward K / K Complex | Ground | utility room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 4 | 4 | 2.24 |  | 1 |  | Manual | Magnetic
512 | Ward K / K Complex | Ground | Kitchen | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 5 | 5 | 5.6 |  | 1 |  | Manual | Magnetic
513 | Ward K / K Complex | Ground | Area 1 | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 5 | 5 | 8.4 |  | 1 |  | Manual | Magnetic
514 | Ward K / K Complex | Ground | Passage 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 5 | 5 | 2.8 |  | 1 |  | Manual | Magnetic
515 | Ward K / K Complex | Ground | Bath Room 2 | Fl. | T12-4 | 4 | 2 | 1 | 2 | 40 | 80 | 6 | 6 | 3.36 |  | 1 |  | Manual | Magnetic
524 | Ward Upper C | First | Nurses' station | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 |  | 2 |  | Manual | Magnetic
525 | Ward Upper C | First | Nurses' station | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 12 | 12 | 3.36
544 | Ward Lower C | Ground | Lobby | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 |  | 1 |  | Manual | Magnetic
545 | Ward Lower C | Ground | Bath Room 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
546 | Ward Lower C | Ground | Eating area | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 |  | 1
547 | Ward Lower C | Ground | Isolating Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
549 | Ward Lower C | Ground | Patient Area 1 | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 8 | 8 | 13.44 |  | 1
550 | Ward Lower C | Ground | Patient Area 2 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 |  | 1
552 | Ward Lower C | Ground | Patient Area 3 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96
553 | Ward Lower C | Ground | Room 1 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 |  | 1
554 | Ward Lower C | Ground | Room 2 | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 8 | 8 | 13.44 |  | 1
555 | Ward Lower C | Ground | Staff Area | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 | 12 | 13.44 |  | 2 |  | Manual | Magnetic
556 | Ward Lower C | Ground | Staff Area | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 | 12 | 13.44 |  | 2 |  | Manual | Magnetic
561 | Ward Villa 1 | Ground | Dormitory | Fl. | T12-4 | 4 | 6 | 2 | 12 | 40 | 480 | 5 | 5 | 16.8 |  | 1 |  | Switch | Electronic Ballast
562 | Ward Villa 1 | Ground | Bath Room | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 |  | 1 |  | Switch | Electronic Ballast
567 | Ward Villa 1 | Ground | Main Corridor | Fl. | T12-4 | 4 | 3 | 2 | 6 | 40 | 240 | 12 | 12 | 20.16 |  | 1 |  | Switch | Electronic Ballast
571 | Ward Villa 2 | Ground | Dormitory | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 |  | 1 | 1 | Switch | Electronic Ballast
573 | Ward Villa 2 | Ground | Dormitory | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 |  |  | 2 | Switch | Electronic Ballast
574 | Ward Villa 2 | Ground | Clothes Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 4 |  | 1.6 |  | 1 | 1 | Switch | Electronic Ballast
575 | Ward Villa 2 | Ground | Passage 1&2 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 | 12 | 13.44 |  | 1 | 1 | Switch | Electronic Ballast
578 | Ward Villa 2 | Ground | Main Corridor | Fl. | T12-4 | 4 | 5 | 2 | 10 | 40 | 400 | 12 | 12 | 33.6 |  | 1 |  | Switch | Electronic Ballast
63 | B Ward | First | Patients’ pantry | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 2 | 2 | 0.56 |  | 1
66 | B Ward | First | Patients’ bathroom | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 2 | 2 | 0.56 |  | 1
73 | Bougain-villea | Ground | Nurse Station | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 12 | 12 | 6.048 |  | 1
74 | Bougain-villea | Ground | Lunch room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 |  | 1
75 | Bougain-villea | Ground | Bath Room/Change Room | Fl. | T12-4 | 4 | 2 | 2 | 4 | 36 | 144 | 2 | 2 | 2.016 |  | 2
76 | Bougain-villea | Ground | Bath Room/Change Room | Fl. | T12-4 | 4 | 1 | 1 | 1 | 36 | 36 | 2 | 2 | 0.504 |  | 1
77 | Bougain-villea | Ground | Treatment room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 12 | 12 | 6.048 |  | 1
96 | CSSD | Ground | CSSD room 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 3 | 0 | 1.08 |  | 1 |  | Manual | Magnetic
162 | Emergency Area | Ground | Doctors Room | Fl. | T12-4 | 4 | 5 | 2 | 10 | 40 | 400 | 12 | 12 | 33.6 |  | 1 | 1 | Switch
163 | Emergency Area | Ground | Treatment Room | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 |  | 1 | 1 | Switch
165 | Hibiscus 1 | Ground | Dining area | Fl. | T12-4 | 4 | 8 | 2 | 16 | 36 | 576 | 12 | 12 | 48.384 |  | 1
172 | Hibiscus 1 | Ground | Treatment room | Fl. | T12-4 | 4 | 2 | 2 | 4 | 36 | 144 | 12 | 12 | 12.096
175 | Hibiscus 1 | Ground | Room 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 |  | 1
179 | Hibiscus 1 | Ground | Lunch Room | Fl. | T12-4 | 4 | 2 | 2 | 4 | 36 | 144 | 12 | 12 | 12.096
181 | Hibiscus 1 | Ground | Passage | Fl. | T12-4 | 4 | 3 | 2 | 6 | 36 | 216 | 12 | 12 | 18.144
183 | Hibiscus 1 | Ground | Corridor | fl. | T12-4 | 4 | 2 | 2 | 4 | 36 | 144 | 12 | 12 | 12.096
184 | Hibiscus 2 | Ground | Pantry | Fl. | T12-4 | 4 | 1 | 1 | 1 | 36 | 36 | 2 | 2 | 0.504 |  | 1
185 | Hibiscus 2 | Ground | Ward | Fl. | T12-4 | 4 | 6 | 2 | 12 | 36 | 432 | 12 | 12 | 36.288 |  | 1
186 | Hibiscus 2 | Ground | Patients’ pantry | Fl. | T12-4 | 4 | 5 | 2 | 10 | 36 | 360 | 2 | 2 | 5.04 |  | 1
188 | Hibiscus 2 | Ground | Nurses Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 12 | 12 | 6.048 |  | 3
189 | Hibiscus 2 | Ground | Patients bathroom | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 |  | 1
191 | Hibiscus 2 | Ground | Passage | Fl. | T12-4 | 4 | 5 | 2 | 10 | 36 | 360 | 12 | 12 | 30.24 |  | 1
229 | Maintenance | Ground | Maintenance office 1 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 12.5 | 12.5 | 3.5 |  | 1 |  | Manual | Magnetic
237 | Maintenance | Ground | Electric-ians' room 2 | Fl. | T12-4 | 4 | 3 | 1 | 3 | 40 | 120 | 9 | 9 | 7.56 |  | 2 |  | Manual | Magnetic
238 | Maintenance | Ground | Male bathroom | Fl. | T12-4 | 4 | 2 | 1 | 2 | 40 | 80 | 3 | 3 | 1.68 |  | 1 |  | Manual | Magnetic
239 | Maintenance | Ground | Female bathroom | Fl. | T12-4 | 4 | 2 | 1 | 2 | 40 | 80 | 4 | 4 | 2.24 |  | 1 |  | Manual | Magnetic
270 | Pharmacy | Ground | Office Cubicle | Fl. | T12-4 | 4 | 6 | 2 | 12 | 40 | 480 | 8 |  | 19.2 |  | 1
271 | Pharmacy | Ground | Room 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1
272 | Pharmacy | Ground | Room 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1
273 | Pharmacy | Ground | Director of Finance | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1
274 | Pharmacy | Ground | File Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 2 |  | 0.8 |  | 1
275 | Pharmacy | Ground | Registry | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1
276 | Pharmacy | Ground | Office | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 |  | 6.4 |  | 1
277 | Pharmacy | Ground | Passage | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 |  | 4.8 |  | 1
279 | Pharmacy | Ground | Vault | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 2 |  | 0.8 |  | 1
281 | Pharmacy | Ground | Accounting Clerk Data Entry | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1
288 | Rainbow Centre | Ground | Room 1 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1
289 | Rainbow Centre | Ground | Room 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1
292 | Rainbow Centre | Ground | Consulting Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
296 | Rainbow Centre | First | Passage | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72
298 | Rainbow Centre | First | Bath Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
299 | Rainbow Centre | First | Sleeping Area | Fl. | T12-4 | 4 | 10 | 2 | 20 | 40 | 800 | 4 | 4 | 22.4 |  | 1
301 | Rainbow Centre | First | Passage | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 |  | 1
303 | Rainbow Centre | First | Kitchen | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 |  | 1
330 | Rock Ward | Ground | Staff Bath Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 |  | 1
346 | Sanitation | Ground | Sanitation super-visor | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 |  | 1
347 | Sanitation | Ground | Trans-portation room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
348 | Sanitation | Ground | Trans-portation super-visor | Fl. | T12-4 | 4 | 4 | 2 | 8 | 40 | 320 | 8 | 8 | 17.92 |  | 1
352 | Sanitation | Ground | House-keeping super-visor | Fl. | T12-4 | 4 | 2 | 1 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
353 | Sanitation | Ground | Room 1 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 |  | 1.6 |  | 1
354 | Sanitation | Ground | Room 2 | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 8 |  | 1.6 |  | 1
358 | Sanitation | Ground | Ground staff room | Fl. | T12-4 | 4 | 6 | 2 | 12 | 40 | 480 | 8 |  | 19.2 |  | 1
366 | Social Work | Ground | Senior Social work office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1
367 | Social Work | Ground | Social work office 1 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 |  | 6.4 |  | 4
369 | Social Work | Ground | Kitchen/ | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 |  | 4.8 |  | 1
370 | Social Work | Ground | Pantry area | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 2 |  | 0.8 |  | 1
371 | Social Work | Ground | Staff bathroom | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1
372 | Social Work | Ground | Social work office 2 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 2
373 | Social Work | Ground | Lobby area (rear) | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 |  | 9.6 |  | 3
402 | Ward 2 | Ground | Bath room 1 & 2 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 |  | 1
404 | Ward 2 | Ground | Room 2,4,5,8,9,12,13,16 | Fl. | T12-4 | 4 | 8 | 2 | 16 | 40 | 640 | 8 | 8 | 35.84 |  | 1
407 | Ward 2 | Ground | Treatment Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
408 | Ward 2 | Ground | Nurse Change Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
409 | Ward 2 | Ground | Nurse Station | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 | 12 | 13.44 |  | 1
411 | Ward 2 | Ground | Clothes Room | Fl. | T12-4 | 4 | 1 | 1 | 1 | 40 | 40 | 2 | 2 | 0.56 |  | 1
412 | Ward 2 | Ground | Area 3 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1
413 | Ward 2 | Ground | Area 4 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 |  | 3.2 |  | 1
415 | Ward 2 | Ground | Eating Area | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 |  | 1
419 | Ward 3 | Ground | Clothes Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
420 | Ward 3 | Ground | Sick Bay | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
423 | Ward 3 | Ground | Room 8, 12 | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96 |  | 1
424 | Ward 3 | Ground | Nurse Station | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 12 | 12 | 13.44 |  | 1
425 | Ward 3 | Ground | Treatment Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
426 | Ward 3 | Ground | Lunch Room | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
427 | Ward 3 | Ground | Office | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1
433 | Ward 3 | Ground | Passage 3 | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72
564 | Ward Villa 1 | Ground | Nurses Lunch | Fl. | T12-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 8 | 8.96
568 | Ward Villa 1 | Ground | Staff Area | LED | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 8 | 8 | 4.48 |  | 1 |  | Switch
570 | Ward Villa 2 | Ground | Nurses Station | Fl. | T12-4 | 4 | 7 | 2 | 14 | 40 | 560 | 12 | 12 | 47.04 |  | 1 | 1 | Switch
161 | Emergency Area | Ground | Corridor | Fl. | T12-4 | 4 | 1 | 2 | 2 | 40 | 80 | 12 | 12 | 6.72 |  | 1
[5 empty] | T12-4 Total |  | 596 |  | 1112 |  | 43686 |  |  | 2429.403 |  |  |  |  | 0
482 | Ward 6 | Ground | Room 15 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1
530 | Ward Upper C | First | Treatment room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 5 | 5 | 1.4 |  | 1 |  | Manual | Magnetic
97 | CSSD | Ground | CSSD bathroom | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 1 | 0 | 0.4 |  | 1 |  | Manual | Magnetic
111 | Day clinic | Ground | Doctors Room 4 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 |  | 1
113 | Day clinic | Ground | Bath Room 2 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 |  | 1
158 | Emergency Area | Ground | Staff Lunch Room | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 8 | 8 | 4.48 |  | 1 | 1 | Switch | Electronic Ballast
197 | In-service education 2 | Ground | Lecture Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 4 |  | 0.8 |  | 1 |  | Manual | Electronic
214 | Laundry | Ground | Passage 1 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36 |  | 1
216 | Laundry | Ground | Room 1 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1
224 | Laundry | Ground | Bath Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1
235 | Maintenance | Ground | Maintenance office 2 | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 | 8 | 1.12 |  | 1 |  | Manual | Electronic
262 | Occupational Therapy | Ground | Bathroom | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 22 | 4 | 4.72 |  | 1
259 | Occupational Therapy | Ground | Staff bathroom | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 8 |  | 3.2 |  | 1
261 | Occupational Therapy | Ground | Patient bathroom | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 |  | 0.8 |  | 1
316 | Rehad Ward | Ground | Bath Room 1 | Fl. | T8-2 | 2 | 2 | 1 | 2 | 20 | 40 | 8 | 8 | 2.24
318 | Rehad Ward | Ground | Room 3,4,5,6,8 & 10 | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 | 8 | 1.12
319 | Rehad Ward | Ground | Room7 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6
321 | Rehad Ward | Ground | Room 12,15,16,18,19 | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 |  | 0.8
322 | Rehad Ward | Ground | Room 11,13,14,17,20 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6
323 | Rehad Ward | Ground | Bath Room 2 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24
326 | Rehad Ward | Ground | Bath Room 3 | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 | 8 | 1.12
328 | Rehad Ward | Ground | Room 22-25 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6
379 | Staff Cafeteria | Ground | Passage 1 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36 |  | 1
384 | Staff Cafeteria | Ground | Areaa 2 & 3 | Fl. | T8-2 | 2 | 6 | 2 | 12 | 20 | 240 | 12 | 12 | 20.16 |  | 1
386 | Staff Cafeteria | Ground | Store Room 2 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 10 | 10 | 2.8 |  | 1 | 1 | Switch | Electronic Ballast
387 | Staff Cafeteria | Ground | Store Room 1 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 10 | 10 | 2.8 |  | 1 | 1 | Switch | Electronic Ballast
503 | Ward K / K Complex | Ground | Room 1 | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 20 | 8 | 8 | 1.12
505 | Ward K / K Complex | Ground | Passage 1 | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 20 | 12 | 12 | 1.68
516 | Ward K / K Complex | Ground | Room 1 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 20 | 6 | 6 | 0.84 |  | 1 |  | Manual | Magnetic
526 | Ward Upper C | First | Water Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 20 | 8 | 8 | 1.12
527 | Ward Upper C | First | Changing Area | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 20 | 8 | 8 | 1.12
529 | Ward Upper C | First | Eating Area | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 6 | 6 | 1.68 |  |  |  | Manual | Magnetic
531 | Ward Upper C | First | Bathroom 1 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 6 | 6 | 1.68 |  | 1 |  | Manual | Magnetic
532 | Ward Upper C | First | Bathroom 2 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 6 | 6 | 1.68 |  | 1 |  | Manual | Magnetic
533 | Ward Upper C | First | Corridor | Fl. | T8-2 | 2 | 6 | 1 | 6 | 20 | 120 | 6 | 6 | 5.04 |  | 1 |  | Manual | Magnetic
534 | Ward Upper C | First | Room 1-17 | Fl. | T8-2 | 2 | 17 | 2 | 34 | 20 | 680 | 6 | 6 | 28.56 |  | 1 |  | Manual | Magnetic
563 | Ward Villa 1 | Ground | Nurses lunch area | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1 |  | Switch | Electronic Ballast
565 | Ward Villa 1 | Ground | Nurses Rest Area | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1 |  | Switch | Electronic Ballast
572 | Ward Villa 2 | Ground | Dormitory | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 8 | 8 | 4.48 |  | 1 | 1 | Switch | Electronic Ballast
576 | Ward Villa 2 | Ground | Staff Rest Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 4 | 4 | 1.12 |  | 1 | 1 | Switch
577 | Ward Villa 2 | Ground | Security Post | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36 |  | 1 | 1 | Switch
108 | Day clinic | Ground | Corridor | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 |  | 1 |  | Manual | Electronic
551 | Ward Lower C | Ground | Patient Area 3 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24
56 | B Ward | First | Main Area | Fl. | T8-2 | 2 | 4 | 2 | 8 | 20 | 160 | 8 | 8 | 8.96 |  | 1
58 | B Ward | First | Patients’ clothes room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 |  | 1
62 | B Ward | First | Pantry | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 2 | 2 | 1.12 |  | 1
64 | B Ward | First | Patients’ pantry | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 2 | 2 | 0.28 |  | 1
67 | B Ward | First | verandah | Fl. | T8-2 | 2 | 3 | 2 | 6 | 20 | 120 | 12 | 12 | 10.08 |  | 1
68 | B Ward | First | verandah | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 12 | 12 | 1.68
84 | Bougain-villea | Ground | Nurse Station | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 12 | 12 | 6.72 |  | 2
92 | Bougain-villea | Ground | Bathroom 2 | Fl. | T8-2 | 2 | 6 | 2 | 12 | 20 | 240 | 8 | 8 | 13.44 |  | 1
85 | Bougain-villea | Ground | Bath Room 3 | Fl. | T8-2 | 2 | 2 | 1 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 2
87 | Bougain-villea | Ground | Bath Room 4 | Fl. | T8-2 | 2 | 2 | 1 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1
91 | Bougain-villea | Ground | Room1-8 | Fl. | T8-2 | 2 | 8 | 2 | 16 | 20 | 320 | 8 | 8 | 17.92 |  | 1
134 | Dietary | Ground | Boiler Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 |  | 1
136 | Dietary | Ground | Dietitic Technician | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 |  | 1
141 | Dietary | Ground | Office 2 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6
151 | Doctor's Lounge | Ground | Restroom | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 4 | 4 | 1.12 |  | 1 | 1 | Switch
166 | Hibiscus 1 | Ground | Patients bathroom | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 8 | 8 | 4.48 |  | 1
167 | Hibiscus 1 | Ground | Clothes room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 |  | 1
168 | Hibiscus 1 | Ground | Staff pantry | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 2 | 2 | 0.28 |  | 1
169 | Hibiscus 1 | Ground | Storage room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 |  | 1
170 | Hibiscus 1 | Ground | Chemical room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 |  | 1
171 | Hibiscus 1 | Ground | Temp Store room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 |  | 1
173 | Hibiscus 1 | Ground | Multi-purpose room | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 2 | 2 | 1.12 |  | 1
174 | Hibiscus 1 | Ground | Nurses’ change room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1
176 | Hibiscus 1 | Ground | Room 2 - 5 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1
177 | Hibiscus 1 | Ground | Staff bathroom | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1
178 | Hibiscus 1 | Ground | Shower Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1
180 | Hibiscus 1 | Ground | Passage | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 12 | 12 | 6.72
182 | Hibiscus 1 | Ground | Corridor | Fl. | T8-2 | 2 | 6 | 2 | 12 | 20 | 240 | 12 | 12 | 20.16 |  | 1
187 | Hibiscus 2 | Ground | Nurses Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36 |  | 2
190 | Hibiscus 2 | Ground | Clothes room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 | 2 | 0.56 |  | 1
212 | Laundry | Ground | Laundry male bathroom | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 3 | 3 | 0.84 |  | 1 |  | Manual | Electronic
213 | Laundry | Ground | Laundry female bathroom | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 3 | 3 | 0.84 |  | 1 |  | Manual | Electronic
278 | Pharmacy | Ground | Passage | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 |  | 2.4 |  | 1
282 | Pharmacy | Ground | Female Bath room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 |  | 1
283 | Pharmacy | Ground | Male Bath Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 |  | 1
293 | Rainbow Centre | Ground | Room 5 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 |  | 1
294 | Rainbow Centre | Ground | Bath Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 |  | 1
295 | Rainbow Centre | First | Passage | Fl. | T8-2 | 2 | 3 | 2 | 6 | 20 | 120 | 12 | 12 | 10.08 |  | 1
297 | Rainbow Centre | First | Staff Lounge | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 |  | 1
300 | Rainbow Centre | First | Sleeping Area | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 8 |  | 3.2 |  | 1
302 | Rainbow Centre | First | Passage | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36 |  | 1
304 | Rainbow Centre | First | Utility Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 2 |  | 0.4 |  | 1
305 | Rainbow Centre | First | Bath Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 |  | 1
306 | Rainbow Centre | First | Staircase | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36 |  | 1
332 | Rock Ward | Ground | Room 3-4- | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6 |  | 1
336 | Rock Ward | Ground | Closet | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 2 |  | 0.2 |  | 1
337 | Rock Ward | Ground | Treatment Room | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 12 | 12 | 1.68
338 | Rock Ward | Ground | Room 5-10 | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 |  | 0.8
339 | Rock Ward | Ground | Visitors Room | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 | 8 | 1.12
341 | Rock Ward | Ground | Room 11-19 | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 | 8 | 1.12
349 | Sanitation | Ground | Bath Room 1 | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 8 | 8 | 4.48 |  | 1
350 | Sanitation | Ground | Passage | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36 |  | 1
351 | Sanitation | Ground | Passage | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 12 | 12 | 1.68
355 | Sanitation | Ground | Bathroom (m) | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1
356 | Sanitation | Ground | Bathroom (f) | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1
357 | Sanitation | Ground | Sanitation bathroom | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1
359 | Sanitation | Ground | Passage | Fl. | T8-2 | 2 | 5 | 1 | 5 | 20 | 100 | 12 | 12 | 8.4 |  | 1
363 | Security House | Ground | Security Post | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36 |  | 1
368 | Social Work | Ground | Social work office 2 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 |  | 1.6
375 | Social Work | Ground | Passage area | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 |  | 2.4 |  | 1
405 | Ward 2 | Ground | Area 1 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1
406 | Ward 2 | Ground | Area 2 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1
410 | Ward 2 | Ground | Nurse Station | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 8 | 8 | 4.48
418 | Ward 3 | Ground | Area 1 | Fl. | T8-2 | 2 | 3 | 1 | 3 | 20 | 60 | 8 | 8 | 3.36 |  | 1
421 | Ward 3 | Ground | Room 1, 3, 4,5,7,9,13,11,12,15 | Fl. | T8-2 | 2 | 10 | 1 | 10 | 20 | 200 | 8 | 8 | 11.2 |  | 1
422 | Ward 3 | Ground | Room 2,6,1014 | Fl. | T8-2 | 2 | 4 | 2 | 8 | 20 | 160 | 8 | 8 | 8.96 |  | 1
428 | Ward 3 | Ground | Room 16 | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 8 | 8 | 1.12 |  | 1
429 | Ward 3 | Ground | Passage 1 | Fl. | T8-2 | 2 | 2 | 2 | 4 | 20 | 80 | 12 | 12 | 6.72 |  | 1
430 | Ward 3 | Ground | Passage 2 | Fl. | T8-2 | 2 | 2 | 1 | 2 | 20 | 40 | 12 | 12 | 3.36
431 | Ward 3 | Ground | Passage 2 | Fl. | T8-2 | 2 | 1 | 1 | 1 | 20 | 20 | 12 | 12 | 1.68 |  | 1
432 | Ward 3 | Ground | Passage 3 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 12 | 12 | 3.36
434 | Ward 3 | Ground | Passage 3 | Fl. | T8-2 | 2 | 2 | 1 | 2 | 20 | 40 | 12 | 12 | 3.36
435 | Ward 3 | Ground | Room 17 | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1
436 | Ward 3 | Ground | Room 18 | fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24
566 | Ward Villa 1 | Ground | Wsh Room | Fl. | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1
579 | Ward Villa 2 | Ground | Patients Bathroom | LED | T8-2 | 2 | 1 | 2 | 2 | 20 | 40 | 8 | 8 | 2.24 |  | 1 | 1 | Switch
[5 empty] | T8-2 Total |  | 207 |  | 364 |  | 7100 |  |  | 385.08 |  |  |  |  | 0
20 | Admin Building | First | Oper-ations Officer 2 | Fl. | T8-4 | 4 | 2 | 2 | 4 | 40 | 160 | 8 | 0 | 6.4 |  | 1 | 1 | Switch | Electronic
115 | Dietary | Ground | Dietitian’s office | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 |  | 2.88 |  | 1
116 | Dietary | Ground | Bathroom (m) | Fl. | T8-4 | 4 | 2 | 2 | 4 | 36 | 144 | 8 | 8 | 8.064 |  | 1
117 | Dietary | Ground | Locker room | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 2 | 2 | 1.008 |  | 1
118 | Dietary | Ground | Bathroom (f) | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 |  | 1
119 | Dietary | Ground | Provision stores office | Fl. | T8-4 | 4 | 2 | 2 | 4 | 36 | 144 | 2 | 2 | 2.016 |  | 1
120 | Dietary | Ground | Store room | Fl. | T8-4 | 4 | 2 | 2 | 4 | 36 | 144 | 2 | 2 | 2.016 |  | 3
121 | Dietary | Ground | Lunch room | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 | 8 | 4.032 |  | 1
122 | Dietary | Ground | Provision cold storage 1 | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 2 | 2 | 1.008 |  | 1
123 | Dietary | Ground | Provision cold storage 2 | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 2 | 2 | 1.008 |  | 1
124 | Dietary | Ground | Provision cold storage 3 | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 2 | 2 | 1.008 |  | 1
125 | Dietary | Ground | Loading bay Passage | Fl. | T8-4 | 4 | 3 | 2 | 6 | 36 | 216 | 2 | 2 | 3.024 |  | 1
126 | Dietary | Ground | Bakery | Fl. | T8-4 | 4 | 2 | 2 | 4 | 36 | 144 | 8 | 8 | 8.064 |  | 1
127 | Dietary | Ground | Liquid meal center | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 12 | 12 | 6.048 |  | 1
128 | Dietary | Ground | Meal Preparation Area | Fl. | T8-4 | 4 | 5 | 2 | 10 | 36 | 360 | 12 | 12 | 30.24 |  | 1
129 | Dietary | Ground | Dietitian’s office | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 |  | 2.88 |  | 1
130 | Dietary | Ground | Main Serving Area | Fl. | T8-4 | 4 | 21 | 2 | 42 | 36 | 1512 | 8 | 8 | 84.672 |  | 1
131 | Dietary | Ground | Serving Area | Fl. | T8-4 | 4 | 2 | 2 | 4 | 36 | 144 | 12 | 12 | 12.096 |  | 1
132 | Dietary | Ground | Passage | Fl. | T8-4 | 4 | 2 | 2 | 4 | 36 | 144 | 12 | 12 | 12.096 |  | 1
133 | Dietary | Ground | Room | Fl. | T8-4 | 4 | 2 | 2 | 4 | 36 | 144 | 8 | 8 | 8.064 |  | 1
135 | Dietary | Ground | Boiler Room | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 2 | 2 | 1.008 |  | 1
137 | Dietary | Ground | Kitchen/ | Fl. | T8-4 | 4 | 3 | 2 | 6 | 36 | 216 | 12 | 12 | 18.144 |  | 1
138 | Dietary | Ground | Store room | Fl. | T8-4 | 4 | 3 | 2 | 6 | 36 | 216 | 2 | 2 | 3.024 |  | 1
139 | Dietary | Ground | Passage way | Fl. | T8-4 | 4 | 1 | 1 | 1 | 36 | 36 | 12 | 12 | 3.024 |  | 1
140 | Dietary | Ground | Office 1 | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 8 |  | 2.88 |  | 1 | [5 empty] | 4.3333
142 | Dietary | Ground | Security Area | Fl. | T8-4 | 4 | 2 | 2 | 4 | 36 | 144 | 12 | 12 | 12.096 |  | 1
143 | Dietary | Ground | Pump Room | Fl. | T8-4 | 4 | 1 | 2 | 2 | 36 | 72 | 2 | 2 | 1.008 |  | 1
[5 empty] | T8-4 Total |  | 66 |  | 131 |  | 4732 |  |  | 241.84 |  |  |  |  | 0
269 | Perimeter Lighting | Pole Mount | Dust to Dawn Light | 175 SVL | X-Security | n/a | 55 | 1 | 55 | 175 | 9625 | 12 | 12 | 808.5
267 | Perimeter Lighting | Pole Mount | Perimeter Lighting | Solar Light | X-Security | n/a | 5 | 1 | 5 | 36 | 180 | 12 | 12 | n/a |  |  |  | Photo-cell
266 | Perimeter Lighting | Pole Mount | LED Perimeter Lighting | 250W HPS | X-Security | n/a | 25 | 1 | 25 | 250 | 6250 | 12 | 12 | 525 |  |  |  | Photo-cell
583 | Perimeter Lighting |  |  | 125W Spot | X-Security | n/a | 2 | 1 | 2 | 125 | 250 | 12 | 12 | 21
[5 empty] | X-Security Total |  | 87 |  | 87 |  | 16305 |  |  | 1354.5 |  |  |  |  | 0
[5 empty] | Grand Total |  | 1084 |  | 1855 |  | 78143 |  |  | 4728.283 | per week |  |  |  | 0
[14 empty] | 20489.2263 | per month
[14 empty] | 245870.716 | per year
| Type | Qty of Fixtures | Qty of Tubes/ Bulbs | Installd Power | Usage kWHrs/ Week | Usage kWHrs/ Month | Usage kWHrs/ Year
EEM-L1 | Bulb Total | 95 | 95 | 4800 | 247.22 | 1071.2867 | 12855.44
EEM-L2 | T12-2 Total | 33 | 66 | 1520 | 70.24 | 304.3733 | 3652.48
EEM-L3 | T12-4 Total | 596 | 1112 | 43686 | 2429.403 | 10527.413 | 126328.956
EEM-L4 | T8-2 Total | 207 | 364 | 7100 | 385.08 | 1668.68 | 20024.16
EEM-L5 | T8-4 Total | 66 | 131 | 4732 | 241.84 | 1047.9733 | 12575.68
EEM-L6 | X-Security | 55 | 55 | 9625 | 808.5 | 3503.5 | 42042
EEM-L7 | X-Security | 5 | 5 | 180 | n/a
EEM-L8 | X-Security | 25 | 25 | 6250 | 525 | 2275 | 27300
EEM-L9 | X-Security | 2 | 2 | 250 | 21 | 91 | 1092
| Totals | 1084 | 1855 | 78143 | 4728.283 | 20489.2263 | 245870.716
Lighting EEM Analysis Bellevue Hospital
EEM No. | Type | Measure | Qty of Tubes | Present Tube Power (W) | Power of New Tube (W) | Previous Annual kWHRS/ Yr | Demand Reduction (kVA) | Energy Saved/yr (kWh) | % Energy Savings | Total Cost Savings/yr (JMD) | Installed Cost (JMD) | SPP (years) | ROI (%/yr) |  | Cost per kWHR | Cost per KVA Demand | ost to change Tube/Bulb | Previous Annual Hours/yr (h) |  | Previous Udage kWHrs | Energy Saved/yr (kWh)
EEM-L1 | Bulb Total | Replace with 20W LEDs | 95 | 50 | 20 | 12855.44 | 2.85 | 7713.264 | 60% | 254391.6 | 237500 | 0.9336 | 107.1% |  | 25 | 1800 | 2500 | 12855.44 |  | 642.772 | 36638.004
EEM-L2 | T12-2 Total | Replace 20W with 13W LEDs | 66 | 20 | 13 | 3652.48 | 0.462 | 1278.368 | 35% | 41938.4 | 165000 | 3.9343 | 25.42% |  | 25 | 1800 | 2500 | 3652.48 |  | 73.0496 | 1687.4458
EEM-L3 | T12-4 Total | Replace with 20W LEDs | 1112 | 40 | 20 | 126328.956 | 22.24 | 63164.478 | 50% | 2059495.95 | 2780000 | 1.3498 | 74.08% |  | 25 | 1800 | 2500 | 126328.956 |  | 5053.1582 | 2809555.9814
EEM-L4 | T8-2 Total | No action | 364 | 20 | 20 | 20024.16 | 0 | 0 | 0% | 0 | 0 |  |  |  | 25 | 1800 |  | 20024.16 |  | 400.4832 | 0
EEM-L5 | T8-4 Total | No action | 131 | 32 | 32 | 12575.68 | 0 | 0 | 0% | 0 | 0 |  |  |  | 25 | 1800 |  | 12575.68 |  | 6169.463 | 0
EEM-L6 | 175 SVL | Replace 175W with 35W LEDs | 55 | 175 | 35 | 42042 | 7.7 | 33633.6 | 80% | 1007160 | 330000 | 0.32765 | 305.2% |  | 25 | 1800 | 6000 | 42042 |  |  | 323723.4
EEM-L7 | Solar Light | No action | 5 | [11 empty] | 25 | 1800 |  | 0 |  |  | 0
EEM-L8 | 250W HPS | Replace with 65W LEDs | 25 | 250 | 65 | 27300 | 4.625 | 20202 | 74% | 604950 | 1625000 | 2.6862 | 37.23% |  | 25 | 1800 | 65000 | 27300 |  |  | 126262.5
EEM-L9 | 125W Spot | Replace with 65W LED | 2 | 125 | 65 | 1092 | 0.12 | 524.16 | 48% | 13104 | 12000 | 0.91575 | 109.2% |  | 25 | 1800 | 6000 | 1092 |  |  | 131.04
| Totals |  | 1855 |  |  | 245870.716 | 37.997 | 126515.87 | 51.46% | 3981039.95 | 5149500 | 1.2935 | 77.31% |  |  |  |  | 245870.716 |  |  | 3297998.3712