| List of working drawings in basic set Page Name Note 1 General Information 2 Fire alarm networks plan Skeleton diagram of fire alarm system 3 Basic diagram and external connection diagram of cutoff during fire List of reference and attached documents Code Title Note Reference documents SNT 3.04.07-94 Administration and domestic buildings SNiP 2.04.09-84 Automatic fire fighting systems in buildings and constructions VSN 60-89 Communication, signaling and Goskomarkhitektura dispatching devices of engineering equipment GOST 21.603-80 Communication and signaling. Working drawings Attached documents ПС.С Specification of equipment, products and materials 2 pages The project is prepared in accordance with effective standards and regulations and provides measures to ensure fire and explosion safety during operation of communication and signaling systems Project chief engineer | General instructions The project provides installation of fire alarm networks. Fire alarm control and indicating equipment of analogue addressable type (Harezmic series) should be used as receiver of automatic fire alarm system. Smoke detectors MG- 9100 and manual alarm call points of button type MG-8100 will be used as endpoints of automatic fire alarm system. Manufacturer of all equipment "Mavi Gard". Alarm actuation is recorded by the control and indicating unit, which gives an alarm signal via electronic sound alarm. Fire alarm control panel will be installed in the airlock entry No.14. Distribution network of fire alarm system should be performed using cable Y(st)-Y 2x2x0.6+0.6 mm2. Power supply network for alarm devices should be provided by laying of NYM cable (24V DS) with cross-section 3x1.5 mm2. Laying of cables should be hidden (in plastic tubes). Uninterruptible power supply unit have to be provided to ensure trouble-proof power supply of fire alarm system. All equipment should conform to state-of-the-art requirements; release date should not be before 2007. NOTE: Positional relationship of all communications will be determined on-site, taking into account ease of installation. Notation conventions Position Surname Signature Date 2013-025-01 – ПС Velayat TB Hospital, Niyazov etrap, Dashoguz city, Turkmenistan Reference laboratory Stage Page Pages total WD 1 3 Prepared by Mamedova M. /signature/ General Information Date: Change: |
| --- | --- |

Sheet size – A3

# Text boxes

Fire alarm control panel

Fire alarm system line

Supply line of alarm devices

Smoke detector

Manual alarm call point

Alarm device

Uninterruptible power supply unit