## Lot2
FORM F: Price Schedule Form
Name of Bidder:
ITB reference:
Date
The Bidder is required to prepare the Price Schedule following the below format. The Price Schedule must include a detailed cost breakdown of all goods and related services to be provided. Separate figures must be provided for each functional grouping or category, if any.
PRICE SCHEDULE
Lot 2- Supply, Delivery, Installation, Testing and Commisioning of 30 Solar off-Grid Systems with capacity of 2.1kWp
BOQ
Item No. | Item Details | Quantity | Unit of Measurment | Unit Cost USD | Total Amount USD | Notes
1 | Solar PV Module:
| Solar PV Array of Total Minimum Capacity 2.1 kWp Mono or Poly Crystalline Silicon. Panel capacity should be ≥350Wp under STC. Positive power tolerance. More than 17 % conversion efficiency under STC. Data sheet of PV module that contains the P-V & I-V Curves, all electrical and mechanical Data, Dimensions, Module area must be provided by bidder. 40°C to 85°C operating temperature range. Temperature Characteristics: Pmax: ≤-0.40% /C° VOC: ≤-0.31% /C° Nominal operating cell temperature (NOCT): 45 ±2°C. The operating voltage of proposed modules should not be less than 1000 VDC. Junction box of IP 67 and heat-resistance bypass diodes. High transparency and transmittance, tempered glass of 3 – 4 mm thickness. Must conform to CE, IEC 61215/ 61730/ 61701/62716, TUV, ISO, UL certificates or equivalent standards. Product warranty for 10 years. Linear performance: Nominal power output not less than 90% after 10 years, 80% after 25 years. | 180 | set
2 | Mounting Structure
| The PV modules shall be mounted on fixed metallic structures having adequate strength and appropriate design, which can withstand the load of the modules and high wind velocities. The support structure shall be hot dip galvanized steel or corrosion resistant aluminum. The structure should be capable of withstanding a wind load of 180 km/hr. The module alignment and tilt angle shall be calculated to provide maximum annual energy output wherever possible. Hot dip galvanized MS mounting structures should be used for mounting the modules / arrays. Minimum thickness of galvanization should be at least 80-120 microns as per ASTM A123 or ASTM A153 and ASTM A385. There should be adequate clearance between module and roofing material to prevent excessive heat being transferred to panels. The elevated structure must be Securely and directly anchored to the concrete rooftop using appropriate size nickel coated steel anchor bolts. Reinforced concrete of appropriate weight if necessary, should be used for anchoring the structure feet’s to keep their resistance for wind load. Bolts, nuts, fasteners, panel mounting clamps should be Stainless steel. Installation: The structures shall be designed for simple mechanical on-site installation. Access for panel cleaning and maintenance All solar panels must be accessible from the top for cleaning and from the bottom for access to the module-junction box. The Installer shall specify installation details of the solar PV modules and the support structures with lay-out drawings and array connection diagrams. Such details shall include, but not limited to, the following: Array tilt angle to the horizontal, Details with drawings for fixing the modules, Structure installation details and drawings, electrical grounding (Earthing). The work shall be carried out as per the designs approved by the UNDP Project engineer. 3 Years product warranty. | 30 | LS
3 | DC Combiner Box
| Combiner Box shall be made of Corrosion resistance material and provided with lockable door and equipped with touch DC fuse-holders, DC fuses, reverse protection diodes, DC surge arrester and load disconnect switches. Installations are expected to last the lifetime warranty of PV modules (about 25 years), so installing durable, long-lived equipment that will stand up to the environment in which it is placed is critical. Combiner box should be Corrosion resistance, Durable, Rust proof, Abrasion resistant, reliable, lockable door, Longer service life, Sun shields (Available from top, sides, and door). Must Include appropriate Output cable Glands &Safety Labels. Outdoor use, double housing, Protection class IP65 and must be waterproof, dustproof, rustproof. 1000 VDC, 15 A Dc input fuse for each String. Input & output string number: as per system design plus 2 spare input strings. Class II SPD with nominal discharge current of 20kA DC MCB with minmum rating of 500 V, 32 A. Operational Environment Temperature of -30 °C ~+70 °C All wires/cables must be terminated through cable lugs. 3 Years product warranty. | 30 | set
4 | Solar Off-Grid Inverter
| Single Phase Off Grid Solar Inverter, Built-in MPPT solar Charge controller. Rated capacity of 3 kW. 230 Vac rated output voltage 50 Hz rated frequency. Less than 3% THD. 24 VDC battery voltage system. Indoor use IP21. -20°C to 55C operation Temperature Range. 5% to 95% Relative Humidity (Non-condensing) Peak efficiency ≥ 90% at full load. Support multistage charging function with possibility to adjust limits of battery charging voltage and charging current. Support connection of other power sources and can monitored remotely. MPPT charge controller of minImum of 3kW @ 24 V DC. AC charging current of Maximum of 60 A. should allow parallel operation, more than one unit can be connected in parallel. Protection: AC overload and short circuit, overvoltage, overheating and battery reverse polarity. Integrated with LCD display and LED status indicator. Not less than 95% MPPT efficiency. Inverter must conform to IEC 62109, CE or equivalent standards. Controller must conform to IEC 62509/ IEC 62093, CE and UL or equivalent standards. 3 Years product warranty. | 30 | set
5 | Battery
| Maintenance free operation 2 V VRLA OPZV type. Minimum capacity of 400/420 Ah @ 10 Hr discharge rate. Battery cyclic performance shall be at least 2500 cycles at 50% depth of discharge (DOD), local or international third party test reports shall be provided proofing the battery lifecycle. 24 Vdc battery bank voltage. Manufacturing date should not be more than 6 months from contracting date. Reliable performance at high operating temperatures of up to 50° C. Self – discharge must be less than 3% per month. 5-12 years battery lifetime. -20 °C ~ +60 °C operating temperature range. Must conform to IEC 60896-22, CE all standards, certificates and Success stories in previous projects. Wires connected to batteries shall utilize appropriately sized and rated lugs or terminals and proper hardware. Batteries shall be installed in a secured, well-ventilated powerhouse. One brand of battery shall be used for the entire installation. 3 years product warranty certificate shall be provided by the manufacturer/Loal representative. Batteries shall be tested in accordance with IEC 61427 standard; | 360 | set
5.1 | Powder coated battery rack with a corrosion resistant acid proof powder with all required accessories as per system voltage. | 30 | set
5.2 | MCB DC breakers box including 1 X 125A 2 P DC breaker, busbar, metal enclosure and all other required accessories. | 30 | Set
6 | System Cables
DC Cables: Soft annealed tin-coated flexible stranded copper per ASTM B-33 and EN 60228. Halogen-free, thermoset polyolefin specifically designed for maximum flexibility. low smoke non-halogenated, flame retardant, oil, abrasion, chemical and sunlight resistant cross-linked compound meeting UL 44, UL 854 and TUV. All cable/wires are to be routed in pipes and suitably tagged and marked with proper manner so that the cable easily identified. Cables should be sized in accordance to IEC 60364-5-52 standard, bidders should indicate cable sizing, and voltage drop calculations considering the following: The total voltage drop on the cable segments from the solar PV modules to the system inverter shall not exceed 3.0%. The total voltage drop on the cable segments from the solar grid inverter to the building distribution board shall not exceed 2.0%. AC Cables Stranded type, TUV certefied, double insulation material 1kV XPLE/PVC/CU, XLPE insulated and PVC seathed single or multi core flexible copper cables meeting IEC 60227 and IEC 60502. The outside PV cables: flexible tinned copper stranded As IEC 60228 , insulated with a special grade PVC or XPLE compound formulated for outdoor use (UV, weather protection). Cable ends connections are to be made through suitable lugs or terminals, crimped properly & with use of cable glands.
6.1 | Cable between array interconnection: 1*6 sqr.mm, 1000 V | 1 | meter
6.2 | Cable between PV module arrays and Combiner box: 1*6 sqr.mm, 1000 V | 1 | meter
6.3 | Cable between combiner box and inverter: 1*25 sqr.mm, 1000 V | 1 | meter
6.4 | Cable Between inverter and Batteries :1*35 sqr.mm, 1000 V | 1 | meter
6.5 | Cable Between Batteries connections:1*35 sqr.mm, 1000 V | 1 | meter
6.6 | Cable between inverter and building ACDB 3*6 sqr.mm | 1 | meter
7 | AC Breaker Boxes
7.1 | MCB AC breakers box including 1 X 25 A 2 P Ac breaker, Battery charging and Ac main sources(utility and backup generator) breaker, busbar, metal enclosure and all other required accessories. Must conform to IEC 60898/60947-2 standard. | 30 | Set
7.2 | Wall mounted Steel Manual transfer switch including metal enclosure, 50 A, 3 poles and must conform to BS EN 60947-3 and should be UL 1008 Listed. | 30 | Set
8 | Cable Tray
| PVC cable tray for indoor and outdoor cables, the size of PVC cable tray depend on number and size of cables to be drawn. HMS grade (1 - 2mm thick), accessories for PVC pipes should have the same characteristics of pipe such as Spacers & Saddles, Couplers, Bends, Tees, Junction boxes for the designated ways and must be adhesive to make all joints rigid. PVC pipes should be Rigid PVC conduits with minimum thickness of 1.5mm to 2.0mm. if necessary, steel cable tray may be used for outside system cables. 3 years product warranty | 1 | meter
9 | Earthing and lightining protection system
| All conductive components of the system shall be earthed using a protective earthing conductor with a minimum CSA of 16 sq.mm. All components that have the potential to experience a differential in voltage (e.g. frames/mounting structures, inverter, combiner box...etc) particularly under fault conditions, shall be equipotential bonded using a bonding conductor. The size of conductor shall be according to table 54.7 of IEE – BS 7671 – IEC 60365-5-54. All system component enclosures, each array structure and all metal casings of the panel, combiner box and inverter shall be connected to the main earth busbar & earthed properly and connected to ground hole. Copper earth rod of 16 or 25 sq. mm x 1200 mm buried in prepared earth pit of 1.2 meters below ground level with 20 kg charcoal & salt. all required acccessorries such as earth pit's cover (Cast Iron cover), cabling, cable lugs...etc. The resistance of Earthing system: Should be less than 3.0 ohm, specially if the area is mountainous, more than one earth rod should be installed in parallel to reduce the earthing resistivity. 3 years product warranty | 30 | Set
Sub Total
|  | Unit | PRICE USD
| Transportation/Delivery Cost | Lump sum
| Bid Total DDP (Incoterms 2010) | Lump sum
| Installation cost | Lump sum
| Operating and maintenance Training (at least for two end users) As mentioned in Scope of Work. | Per Facility/ Location
| Warranty period as mentioned above | Lump sum
| After Sales as mentioned in the scope of work | Per Facility/ Location
GRAND TOTAL
Name of Bidder:
Authorised signature:
Name of authorised signatory:
Functional Title: