## BoQ
INTELLIGENT AND ADDRESSABLE FIRE ALARM SYSTEM AT UNDP, PULCHOWK, LALITPUR, NEPAL
Bill of Quantity And Budget
Essential Components For Fire Detection and Alarm System
| S.No. | Description | Unit | Quantity | Unit Rate(NPR) | Amount(NPR) | Amount(USD) | CIF AMOUNT(USD)
| 1 | Intelligent addressable 2 Loop Main Fire alarm panel complete with sufficient number of loops to accommodate all the BOQ quantity with atleast 10% spare capacity LCD/VGA display with Keypad or Touch Screen, Zonal LED indication, Network communication module for peer networking of more panels, Repeater interface, Ethernet port and power supply unit with battery back-up for atleast 30 min during alarm and 12 hours standby. Each loop should be capable of accommodating all the detectors and devices.(Loop1: 250, Loop 2: 120) | Set | 1
(Bidder may propose panels / loop configuration as per manufacturers recommendation to meet overall project requriement plus provision for 2 future loop.)
| 2 | Intelligent addressable photoelectric smoke detector with base. | Set | 223
(include Fault Isolation Module if not Included)
| 3 | Intelligent addressable heat detectors with base. | Set | 10
(include Fault Isolation Module if not Included)
| 4 | Addressable Manual Call point complete set boxes. As per speficifications. | Set | 25
| 5 | Surface mounted addressable type Sounder cum strobe. | Set | 32
| 6 | 2 x 1.5 sq mm twisted PVC copper conductor flexible cable in PVC Conduit. Including Saddles, Connectors, Junction Box etc. cable accessories, Screw, Grip,etc. | RM | 3600
| 7 | 4 x 1.5 sq MM Armoured Cable for Outdoor including Saddles, Connectors, Junction Box, cable accessories, Screw, Grip,etc. | RM | 600
| 8 | Supply, installation, testing, training and commissioning and handing over of fully integrated addressable fire alarm system: | Lumpsum
(Including, Drilling, digging, Cementing, Civil Work etc.)
| 9 | Repeater panel | Nos | 1
| 10 | Cat6 Cable or Cables as per the Requirement | RM | 300
| 11 | Socket Extension for Local Power | Set | 1
| 12 | Supply, installation, testing, training and commissioning and handing over of Repeater Panel | Lumpsum
Total
Public Annoucement System
Manual PA Based System
| S.No. | Description | Unit | Quantity | Unit Rate | Amount | Amount(USD) | CIF AMOUNT(USD)
| 1 | Main Public address panel with following configuration: - Wall Mount Rack - 600W booster amplifier | Set | 1
| 2 | Power Backup to Operate the System for 2 Hours | Set | 1
Speakers: Indoor Speakers
| 3 | Ceiling Speakers minimum 80db at 1 meter | Nos | 33
| 4 | Wall Speakers minimum 80db at 1 meter | Nos | 16
| 5 | 2 x 1.5 sq mm twisted PVC copper conductor flexible cable in PVC Conduit. Including Saddles, Connectors, Junction Box etc. cable accessories, Screw, Grip etc. | RM | 2000
Speakers: Outdoor Speakers
| 6 | Outdoor Speakers minimum 80db at 1 meter | Nos | 10
| 7 | 2 x 1.5 sq mm twisted PVC copper conductor flexible cable in PVC Conduit. Including Saddles, Connectors, Junction Box etc. cable accessories, Screw, Grip etc. | RM | 400
Installation
| 8 | Supply, installation, testing, training and commissioning and handing over of PA System | Lumpsum
Total