## Sheet1
Full Rehabilitation of Al-Tarboliya Sub PHCC in Al-Khairat District
Item # in BOQ | Item |  | Description | Required Specifications | Offered Specifications
81 - A | Air-Conditioning Split Units of 1.5 Ton Capacity |  | Manufacturer Name: | Tosot , York or equivalent which should be approved by the supervisory committee before starting supplying process
|  |  | Type: | Heating and cooling and Wall Mounted Split Unit
|  |  | Auxiliary supply voltage (V): | 230 V/50HZ
|  |  | Tonnage Range (T): | 1.5 Ton
|  |  | Compressor: | Inverter / T3
|  |  | Refrigerant Gas: | R410A
|  |  | Cooling and Heating Capacity (BTUH): | 18000
|  |  | Filter Type: | Micro dust protection filter washable
|  |  | Running current (A): | As Manufacture
|  |  | Operation Range temperature ©: | 17 -30
|  |  | Remote Control: | Wireless /LCD type
|  |  | Noise Level (dB): | 30 - 35 -40
|  |  | Max ambient temp.: | T3 (54°C)
|  |  | Certification of origin: | Yes/Required
|  |  | Submit Manufacturer certification and test reports: | Yes/Required
|  |  | Submit Detail drawing brochure catalogue.: | Yes/Required
81-B | Air-Conditioning Split Units of 2 Ton Capacity |  | Manufacturer Name: | Tosot or York or equivalent which should be approved by the supervisory committee before starting supplying process
|  |  | Type: | Heating and cooling and Wall Mounted Split Unit
|  |  | Auxiliary supply voltage (V): | 230 V/50HZ
|  |  | Tonnage Range (T): | 2 Ton
|  |  | Compressor: | Inverter / T3
|  |  | Refrigerant Gas: | R410A
|  |  | Cooling and Heating Capacity (BTUH): | 24000
|  |  | Filter Type: | Micro dust protection filter washable
|  |  | Running current (A): | As Manufacture
|  |  | Operation Range temperature ©: | 17 -30
|  |  | Remote Control: | Wireless /LCD type
|  |  | Noise Level (dB): | 30 - 35 -40
|  |  | Max ambient temp.: | T3 (54°C)
|  |  | Certification of origin: | Yes/Required
|  |  | Submit Manufacturer certification and test reports: | Yes/Required
|  |  | Submit Detail drawing brochure catalogue.: | Yes/Required
82 | Air-Conditioning Split Units of 3 Ton Capacity |  | Manufacturer Name: | Tosot , York or equivalent which should be approved by the supervisory committee before starting supplying process
|  |  | Type: | Heating and cooling Vertical Split Unit (Floor Standing Type)
|  |  | Auxiliary supply voltage (V): | 380 V/50HZ
|  |  | Tonnage Range (T): | 3 Ton
|  |  | Compressor: | Inverter / T3
|  |  | Refrigerant Gas: | R410A
|  |  | Cooling and Heating Capacity (BTUH): | 36000
|  |  | Filter Type: | Micro dust protection filter washable
|  |  | Running current (A): | As Manufacture
|  |  | Operation Range temperature ©: | 17 -30
|  |  | Remote Control: | Wireless /LCD type
|  |  | Noise Level (dB): | 30 - 35 -40
|  |  | Max ambient temp.: | T3 (52°C)
|  |  | Certification of origin: | Yes/Required
|  |  | Submit Manufacturer certification and test reports: | Yes/Required
|  |  | Submit Detail drawing brochure catalogue.: | Yes/Required
83 | Air-Conditioning Split Units of 4 Ton Capacity |  | Manufacturer Name: | Tosot , York or equivalent which should be approved by the supervisory committee before starting supplying process
|  |  | Type: | Heating and cooling Vertical Split Unit (Floor Standing Type)
|  |  | Auxiliary supply voltage (V): | 380 V/50HZ
|  |  | Tonnage Range (T): | 4 Ton and Three phases
|  |  | Compressor: | Rotary / T3
|  |  | Refrigerant Gas: | R410A
|  |  | Cooling and Heating Capacity (BTUH): | 48000
|  |  | Filter Type: | Micro dust protection filter washable
|  |  | Running current (A): | As Manufacture
|  |  | Operation Range temperature ©: | 17 -30
|  |  | Remote Control: | Wireless /LCD type
|  |  | Noise Level (dB): | 30 - 35 -40
|  |  | Max ambient temp.: | T3 (52°C)
|  |  | Certification of origin: | Yes/Required
|  |  | Submit Manufacturer certification and test reports: | Yes/Required
|  |  | Submit Detail drawing brochure catalogue.: | Yes/Required
84 | Electrical Water Heater 160 Liter capacity |  | Type: | Electrical water boiler 160 liter with two heater 3000 Wat
|  |  | Installation: | Vertical /Cylindrical
|  |  | Water Tank Coating: | Enameled
|  |  | Capacity Range: | 160 Liter
|  |  | Electric heating type | Two Immersion element of 3000 Watt Italian origin or equivalent which should be approved by the supervisory committee before starting supplying process
|  |  | The thickness of internal basin walls | Not less than 2.5 mm
|  |  | Nominal power: | 220v-240v /50HZ
|  |  | Nominal pressure: | 0.8 Mpa
|  |  | In let & out let Decimeter: | ¾ “Inch
|  |  | Electric heating type: | Immersion element
|  |  | Insulation Type: | Foam
|  |  | Protection: | Safety Valve ¾”
|  |  | Submit Manufacturer certification and test reports: | Yes/Required
|  |  | Submit Detail drawing brochure catalogue: | Yes/Required
85 | Water pump |  | Origin : | Italian, German origin or equivalent which should be approved by the supervisory committee before starting supplying process
A-Motor:
|  |  | Rated voltage: | 220V – 240V
|  |  | No of phase: | 1PH with capacitor
|  |  | Frequency: | 50 Hz
|  |  | Rated speed: | 2900 RPM
|  |  | Rated power: | 1.5 Kwatt
|  |  | Cos phi power factor: | 0.80 - 0.90
|  |  | Start method: | Normal Start
|  |  | Enclosure class: | (IEC 34-1)( protect water jet, mud and dust)IP 55
|  |  | Insulation class: | F
|  |  | Motor Protect: | Full motor protection
|  |  | Thermal Protection: | Full motor protection
|  |  | Built-in temperature transmitter: | Yes
|  |  | Max ambient temp.: | 60°C
B- Pump section
|  |  | Type: | Centrifugal horizontal Pump electrically controlled
|  |  | Pump liquid: | Clean water
|  |  | Rated flow: | 3 m3/hr.
|  |  | Rated head: | 15 M
|  |  | Pump Body: | Cast Iron with threaded ports ISO 228/1
|  |  | Shaft Materials: | Stainless Steel 1.4404
|  |  | Impeller Material: | Brass, radial Peripheral Vanes.
86 | Stainless Steel Water Cooler |  | Type: | Free standing Cold Drinking Water Dispenser
|  |  | Brand | Al Sabeel , DANA or equivalent which should be approved by the supervisory committee before starting supplying process
|  |  | Capacity: | 90 Litter
|  |  | Cooling water capacity : | 90 Litter per hour up to 5 Degrees
|  |  | Material of Tank: | Stainless steel 316
|  |  | Dip Tray: | Stainless steel 304
|  |  | Number of Taps: | 4 Taps
|  |  | Type of Tap: | Push cocks
|  |  | Compressor Capacity: | 1/2 HP
|  |  | Type: | Rotary
|  |  | Refrigerant Gas: | R410a
|  |  | Voltage: | 220v -240v/50HZ
|  |  | Certification of origin: | Yes/Required
|  |  | Submit Manufacturer certification and test reports: | Yes/Required
87 | 7 Stage RO Filter |  | Origin: | Taiwanese, Korean, American origin or equivalent which should be approved by the supervisory committee before starting supplying process
Consist of:
|  |  | One 5 Micron Polypropylene Sediment Filter PP. | One 5 Micron Polypropylene Sediment Filter PP.
|  |  | One Granule Activated Carbon Filter (GAC) - Chlorine and Lime. | One Granule Activated Carbon Filter (GAC) - Chlorine and Lime.
|  |  | One 1 Micron Activated Carbon Block Filter (CTO). | One 1 Micron Activated Carbon Block Filter (CTO).
|  |  | One Fullcome Membrane 50 GPD - 0,0001 Micron. | One Fullcome Membrane 50 GPD - 0,0001 Micron.
|  |  | One Post Inline Carbon Filter. | One Post Inline Carbon Filter.
|  |  | One Alkaline Re-Mineralization Filter. | One Alkaline Re-Mineralization Filter.
|  |  | One UV Sterilization Filter. | One UV Sterilization Filter.
|  |  | One Storage Tank 10 Liters, RO Pipe 5 Meters, Connection fitting 15mm. | One Storage Tank 10 Liters, RO Pipe 5 Meters, Connection fitting 15mm.
93 | Distribution Transformer 11/0.416 kV 250 KVA |  | 1- Make/Brand/Model: | To be filled
|  |  | 2- Manufacturer Name: | To be filled
|  |  | 3- Type: | Oil-immersed hermetically sealed - bolted type- three phase-outdoor
|  |  | 4- Country of origin | Turkish , KSA origin or equivalent which should be approved by the supervisory committee before starting supplying process
|  |  | 5- Reference standard | IEC 60076-1, 2,3,5,8, IEC 60214, IEC 60137
|  |  | 6- Ambient temperature: | Maximum:55/C Minimum: -10/C
|  |  | 7- Air humidity: | 92% maximum
|  |  | 8- Altitude: | 1000M above MSL
|  |  | 9- Highest system voltage | 12 kV
|  |  | 10- 1Short circuit current on 11 kV side | 25 KA
|  |  | 11- 11 kV system earthing | Neutral isolated / earthed through a resistor
|  |  | 12- Low voltage side earthing | Neutral solidly earthed
|  |  | 13- Voltage Ratio | 11/0.416 KV
|  |  | 14- Type of cooling | ONAN
|  |  | 15- Rated power - Continuous | 250 kVA
|  |  | 16- Rated Frequency | 50Hz
|  |  | 17- Impedance voltage at 75 deg at nominal tap | ≥ 4%
18- Nominal Voltage of winding
|  |  | A- H.V. | 11 kV
|  |  | B- L.V | 0.416 kV
19- Insulation level 11 kV
|  |  | A- Lightning Impulse | 75 kV
|  |  | B- AC power frequency | 28 kV
|  |  | 20- Insulation level LV -phases/neutral AC power frequency | 3 kV
|  |  | 21- Winding temperature rise at rated power | 50 C
|  |  | 22- Top oil temperature rise at rated power | 45 C
|  |  | 23- No load loss in | KW
|  |  | 24- Load loss at full load at 75 deg temperature | Kw
|  |  | 25- Efficiency | ≥98.6%
|  |  | 26- Regulation | To be filled
|  |  | 27- Maximum flux density in iron at rated frequency and at rated voltage ratio at nominal voltage | ≤ 1.65 Tesla
28- Maximum current density in windings at rated power
|  |  | A- H.V. winding | To be filled
|  |  | B- L.V. winding | To be filled
|  |  | 29- No load current at rated voltage | Amp
|  |  | 30- Material of windings | Copper
31- Type of insulation of
|  |  | A- Core assembly | To be filled
|  |  | B- Core laminations | To be filled
32- Thickness of transformer
|  |  | A- tank | Minimum 3 mm
|  |  | B- sides | Minimum 3 mm
|  |  | C- bottom | Minimum 3 mm
|  |  | 33- Thickness of radiator plates and for cooling tube | Minimum 1.2 mm
34- Winding connection
|  |  | A- H.V. | Delta
|  |  | B- L.V. | Star (Neutral brought out)
|  |  | 35- Vector group symbol | Dyn11
|  |  | 36- Tap changer | Off-load tap changer with 5 positions in the HV winding giving ± 2 x 2.5 %.
|  |  | 37- 11 kV side terminal arrangement | Clamp type for terminating up to 150 mm2 copper conductor
|  |  | 38- Low voltage terminal arrangement | Suitable for terminating copper cables of cross section area 6x1x95+1x70 mm2( 1 hole per phase )
|  |  | 39- Noise level at 0.3 m distance | ≤ 55 dB
|  |  | 40- Transformer oil | To be filled
|  |  | A-Type of oil | IEC60296 class 1
|  |  | B-Manufacturer | To be filled
|  |  | C- Place of manufacture | To be filled
|  |  | D-Manufacturer’s type designation | To be filled
|  |  | E-Applied IEC standard | IEC 60296
F- Kinematic viscosity mm2/s
|  |  | F-1/ At 40 deg | ≤ 16.5
|  |  | F-2/ At -15 deg | ≤ 800
|  |  | G- Flash point | ≥ 140 C
|  |  | H- Pour point | ≤ - 30 C
|  |  | I- Density at 20 deg C – kg/dm3 | ≤ 0.895
|  |  | J- Breakdown strength | kV
|  |  | 41- Dimensions of transformer | L 1230 ( mm) x W 700.(mm) x H 1300.(mm)
|  |  | 42- Weight of transformer | kg
43- Type of corrosion protection on steel parts
|  |  | A- Inside tank | Oil resistant paint
|  |  | B- Outside tank | Metalized, aluminium paint or equivalent
44- 11 kV bushings
|  |  | A- Name of manufacturer | To be filled
|  |  | B- Make/Brand/Model: | To be filled
|  |  | C- Refrence standard | IEC 60137
|  |  | D- Type of bushing | To be filled
|  |  | E- Rated current | Amp
|  |  | F- Rated voltage | KV
|  |  | G- Material | Porcelain
|  |  | H- Color | Brown
|  |  | I- Creepage distance | Minimum 300 mm
45- L V bushings
|  |  | A- Name of manufacturer | To be filled
|  |  | B- Make/Brand/Model: | To be filled
|  |  | C- Reference standard | IEC 60137
D- Type of bushing
|  |  | E- Rated current | Amp
|  |  | F- Rated voltage | KV
|  |  | G- Material | Porcelain
|  |  | H- Color | Brown
|  |  | I- Creepage distance | mm
|  |  | 46- Warranty period | One year
|  |  | 47- Submit manufacturers certification | Yes /required
|  |  | 48- Submit type test certificates or reports: | Yes /required
|  |  | 49- Submit Detail drawings, drawings of HV and LV bushings, details of accessories, brochures and catalogues: | Yes /required
105 | Electrical Generator of 150 kVA Capacity |  | Manufacturer: | Original manufacturer (Local Assembled Not acceptable)
|  |  | Type: | Silent type
|  |  | Required Brand: | Perkins , caterpillar or equivalent which should be approved by the supervisory committee before starting supplying process
|  |  | Engine brand name | To be filed
|  |  | Engine model number | To be filed
|  |  | Alternator brand name | To be filed
|  |  | Alternator model number | To be filed
|  |  | Ambient temperature: | Maximum:55/C & Minimum: -10/C
|  |  | Relative Humidity: | Around 60% at maximum temperature
|  |  | Altitude: | 1000 M above MSL
|  |  | System Voltage: | 400V/ 3PH, 50 HZ
|  |  | Guarantee: | One year or 1000HR / operation
|  |  | Generator output Range: | 150 KVA prime
|  |  | Exhaust Type: | Exhaust and inlet/outlet air
|  |  | Stand by: | Not less 165 KVA, 400A 4pole and 8-hour operation base tank
|  |  | No of cylinders: | 6 inline
|  |  | Speed max: | 1500 RPM and Electronic Governor
|  |  | Fuel system: | Fuel system/storage Diesel tanks
|  |  | Battery system: | Type of starting 24 DC Battery system
|  |  | Power factor: | Between 0.8 and 1
|  |  | Type of excitation: | Brushless, self-regulation and separately exited
|  |  | Cooling type: | Water cooled
|  |  | No. of cycle: | Six cycle
|  |  | Turbocharged: | Turbocharged
|  |  | Enclosure class: | Not less than 23
|  |  | Insulation class: | Class H
|  |  | Earthingstuds: | Yes/ Required
|  |  | Test: | Yes/Required
|  |  | Certificate of origin and inspection documents: | Yes/ Required
Name of Bidder: ______________________________
Authorized signature: ______________________________
Functional Title: ______________________________
Company: ______________________________
Date: ______________________________