{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Sheet1"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":263,"n_cols":9,"rows_kept":263,"cut":false,"hidden":false,"merged":[[103,0,116,0],[103,1,116,2],[221,0,249,0],[221,1,249,2],[117,0,126,0],[117,1,126,2],[127,0,220,0],[127,1,220,2],[0,0,0,5],[80,0,102,0],[66,1,79,2],[66,0,79,0],[1,1,1,2],[80,1,102,2],[2,0,17,0],[2,1,17,2],[18,0,33,0],[18,1,33,2],[34,0,49,0],[34,1,49,2],[50,0,65,0],[50,1,65,2]]}
["Full Rehabilitation of Al-Tarboliya Sub PHCC in Al-Khairat District"]
["Item # in BOQ","Item",null,"Description ","Required Specifications","Offered Specifications"]
["81 - A"," Air-Conditioning Split Units of 1.5 Ton Capacity",null,"Manufacturer Name:  ","Tosot , York or equivalent which should be approved by the supervisory committee before starting supplying process"]
[null,null,null,"Type: ","Heating and cooling and Wall Mounted Split Unit "]
[null,null,null,"Auxiliary supply voltage (V):","230 V/50HZ "]
[null,null,null,"Tonnage Range (T):","1.5 Ton "]
[null,null,null,"Compressor: ","Inverter / T3 "]
[null,null,null,"Refrigerant Gas: ","R410A "]
[null,null,null,"Cooling and Heating Capacity (BTUH): ",18000]
[null,null,null,"Filter Type:","Micro dust protection filter washable "]
[null,null,null,"Running current (A):","As Manufacture "]
[null,null,null,"Operation Range temperature ©:"," 17 -30 "]
[null,null,null,"Remote Control:","Wireless /LCD type "]
[null,null,null,"Noise Level (dB):","30 - 35 -40 "]
[null,null,null,"Max ambient temp.:","T3 (54°C) "]
[null,null,null,"Certification of origin:","Yes/Required"]
[null,null,null,"Submit Manufacturer certification and test reports:  ","Yes/Required"]
[null,null,null,"Submit Detail drawing brochure catalogue.: ","Yes/Required"]
["81-B"," Air-Conditioning Split Units of 2 Ton Capacity",null,"Manufacturer Name:  ","Tosot or York or equivalent which should be approved by the supervisory committee before starting supplying process"]
[null,null,null,"Type: ","Heating and cooling and Wall Mounted Split Unit "]
[null,null,null,"Auxiliary supply voltage (V):","230 V/50HZ "]
[null,null,null,"Tonnage Range (T):","2 Ton "]
[null,null,null,"Compressor: ","Inverter / T3 "]
[null,null,null,"Refrigerant Gas: ","R410A "]
[null,null,null,"Cooling and Heating Capacity (BTUH): ",24000]
[null,null,null,"Filter Type:","Micro dust protection filter washable "]
[null,null,null,"Running current (A):","As Manufacture "]
[null,null,null,"Operation Range temperature ©:"," 17 -30 "]
[null,null,null,"Remote Control:","Wireless /LCD type "]
[null,null,null,"Noise Level (dB):","30 - 35 -40 "]
[null,null,null,"Max ambient temp.:","T3 (54°C) "]
[null,null,null,"Certification of origin:","Yes/Required"]
[null,null,null,"Submit Manufacturer certification and test reports:  ","Yes/Required"]
[null,null,null,"Submit Detail drawing brochure catalogue.: ","Yes/Required"]
[82," Air-Conditioning Split Units of 3 Ton Capacity",null,"Manufacturer Name:  ","Tosot , York  or equivalent which should be approved by the supervisory committee before starting supplying process"]
[null,null,null,"Type: ","Heating and cooling Vertical Split Unit (Floor Standing Type)"]
[null,null,null,"Auxiliary supply voltage (V):","380 V/50HZ "]
[null,null,null,"Tonnage Range (T):","3 Ton"]
[null,null,null,"Compressor: ","Inverter / T3 "]
[null,null,null,"Refrigerant Gas: ","R410A "]
[null,null,null,"Cooling and Heating Capacity (BTUH): ",36000]
[null,null,null,"Filter Type:","Micro dust protection filter washable "]
[null,null,null,"Running current (A):","As Manufacture "]
[null,null,null,"Operation Range temperature ©:"," 17 -30 "]
[null,null,null,"Remote Control:","Wireless /LCD type "]
[null,null,null,"Noise Level (dB):","30 - 35 -40 "]
[null,null,null,"Max ambient temp.:","T3 (52°C) "]
[null,null,null,"Certification of origin:","Yes/Required"]
[null,null,null,"Submit Manufacturer certification and test reports:  ","Yes/Required"]
[null,null,null,"Submit Detail drawing brochure catalogue.: ","Yes/Required"]
[83," Air-Conditioning Split Units of 4 Ton Capacity",null,"Manufacturer Name:  ","Tosot , York  or equivalent which should be approved by the supervisory committee before starting supplying process"]
[null,null,null,"Type: ","Heating and cooling Vertical Split Unit (Floor Standing Type)"]
[null,null,null,"Auxiliary supply voltage (V):","380 V/50HZ "]
[null,null,null,"Tonnage Range (T):","4 Ton and Three phases "]
[null,null,null,"Compressor: ","Rotary / T3 "]
[null,null,null,"Refrigerant Gas: ","R410A "]
[null,null,null,"Cooling and Heating Capacity (BTUH): ",48000]
[null,null,null,"Filter Type:","Micro dust protection filter washable "]
[null,null,null,"Running current (A):","As Manufacture "]
[null,null,null,"Operation Range temperature ©:"," 17 -30 "]
[null,null,null,"Remote Control:","Wireless /LCD type "]
[null,null,null,"Noise Level (dB):","30 - 35 -40 "]
[null,null,null,"Max ambient temp.:","T3 (52°C) "]
[null,null,null,"Certification of origin:","Yes/Required"]
[null,null,null,"Submit Manufacturer certification and test reports:  ","Yes/Required"]
[null,null,null,"Submit Detail drawing brochure catalogue.: ","Yes/Required"]
[84,"Electrical Water Heater 160 Liter capacity",null,"Type: ","Electrical water boiler 160 liter with two heater 3000 Wat"]
[null,null,null,"Installation: ","Vertical /Cylindrical"]
[null,null,null,"Water Tank Coating: ","Enameled"]
[null,null,null,"Capacity Range: ","160 Liter"]
[null,null,null,"Electric heating type","Two Immersion element of 3000 Watt Italian origin or equivalent which should be approved by the supervisory committee before starting supplying process"]
[null,null,null,"The thickness of internal basin walls ","Not less than 2.5 mm "]
[null,null,null,"Nominal power: ","220v-240v /50HZ"]
[null,null,null,"Nominal pressure: ","0.8 Mpa"]
[null,null,null,"In let & out let Decimeter: ","¾ “Inch"]
[null,null,null,"Electric heating type:","Immersion element"]
[null,null,null,"Insulation Type: ","Foam"]
[null,null,null,"Protection: ","Safety Valve ¾”"]
[null,null,null,"Submit Manufacturer certification and test reports: ","Yes/Required"]
[null,null,null,"Submit Detail drawing brochure catalogue:  ","Yes/Required"]
[85,"Water pump",null,"Origin :","Italian, German origin or equivalent which should be approved by the supervisory committee before starting supplying process"]
[null,null,null,"A-Motor:                                     "]
[null,null,null,"Rated voltage: ","220V – 240V"]
[null,null,null,"No of phase: ","1PH with capacitor "]
[null,null,null,"Frequency:","50 Hz"]
[null,null,null,"Rated speed: ","2900 RPM"]
[null,null,null,"Rated power: ","1.5 Kwatt"]
[null,null,null,"Cos phi power factor: ","0.80 - 0.90"]
[null,null,null,"Start method: ","Normal Start "]
[null,null,null,"Enclosure class: ","(IEC 34-1)( protect water jet, mud and dust)IP 55"]
[null,null,null,"Insulation class:"," F"]
[null,null,null,"Motor Protect:"," Full motor protection"]
[null,null,null,"Thermal Protection: ","Full motor protection"]
[null,null,null,"Built-in temperature transmitter: ","Yes"]
[null,null,null,"Max ambient temp.:","60°C"]
[null,null,null,"B- Pump section"]
[null,null,null,"Type:","Centrifugal horizontal Pump electrically controlled"]
[null,null,null,"Pump liquid:","Clean water"]
[null,null,null,"Rated flow: "," 3 m3/hr."]
[null,null,null,"Rated head: ","15 M"]
[null,null,null,"Pump Body: ","Cast Iron with threaded ports ISO 228/1"]
[null,null,null,"Shaft Materials: ","Stainless Steel 1.4404"]
[null,null,null,"Impeller Material:  ","Brass, radial Peripheral Vanes."]
[86,"Stainless Steel Water Cooler ",null,"Type:"," Free standing Cold Drinking Water Dispenser "]
[null,null,null,"Brand","Al Sabeel , DANA or equivalent which should be approved by the supervisory committee before starting supplying process"]
[null,null,null,"Capacity: ","90 Litter"]
[null,null,null,"Cooling water capacity :","90 Litter per hour up to 5 Degrees "]
[null,null,null,"Material of Tank: ","Stainless steel 316 "]
[null,null,null,"Dip Tray: ","Stainless steel 304"]
[null,null,null,"Number of Taps: ","4 Taps"]
[null,null,null,"Type of Tap: ","Push cocks"]
[null,null,null,"Compressor Capacity: ","1/2 HP"]
[null,null,null,"Type: ","Rotary"]
[null,null,null,"Refrigerant Gas: ","R410a"]
[null,null,null,"Voltage: ","220v -240v/50HZ"]
[null,null,null,"Certification of origin:  ","Yes/Required"]
[null,null,null,"Submit Manufacturer certification and test reports:","Yes/Required"]
[87,"7 Stage RO Filter",null,"Origin:  ","Taiwanese, Korean, American origin or equivalent which should be approved by the supervisory committee before starting supplying process"]
[null,null,null,"Consist of:"]
[null,null,null,"One 5 Micron Polypropylene Sediment Filter PP.","One 5 Micron Polypropylene Sediment Filter PP."]
[null,null,null,"One Granule Activated Carbon Filter (GAC) - Chlorine and Lime.","One Granule Activated Carbon Filter (GAC) - Chlorine and Lime."]
[null,null,null,"One 1 Micron Activated Carbon Block Filter (CTO).","One 1 Micron Activated Carbon Block Filter (CTO)."]
[null,null,null,"One Fullcome Membrane 50 GPD - 0,0001 Micron.","One Fullcome Membrane 50 GPD - 0,0001 Micron."]
[null,null,null,"One Post Inline Carbon Filter.","One Post Inline Carbon Filter."]
[null,null,null,"One Alkaline Re-Mineralization Filter.","One Alkaline Re-Mineralization Filter."]
[null,null,null,"One UV Sterilization Filter.","One UV Sterilization Filter."]
[null,null,null,"One Storage Tank 10 Liters, RO Pipe 5 Meters, Connection fitting 15mm.","One Storage Tank 10 Liters, RO Pipe 5 Meters, Connection fitting 15mm."]
[93,"Distribution Transformer 11/0.416 kV 250 KVA",null,"1- Make/Brand/Model:","To be filled"]
[null,null,null,"2- Manufacturer Name:  ","To be filled"]
[null,null,null,"3- Type: ","Oil-immersed hermetically sealed - bolted type- three phase-outdoor"]
[null,null,null,"4- Country of origin","Turkish , KSA origin or equivalent which should be approved by the supervisory committee before starting supplying process"]
[null,null,null,"5- Reference standard","IEC 60076-1, 2,3,5,8, IEC 60214, IEC 60137"]
[null,null,null,"6- Ambient temperature:","Maximum:55/C                                                                                         Minimum: -10/C\n"]
[null,null,null,"7- Air humidity:","92% maximum "]
[null,null,null,"8- Altitude:","1000M above MSL"]
[null,null,null,"9- Highest system voltage","12 kV "]
[null,null,null,"10- 1Short circuit current on 11 kV side ","25 KA "]
[null,null,null,"11- 11 kV system earthing ","Neutral isolated / earthed through a resistor"]
[null,null,null,"12- Low voltage side earthing ","Neutral solidly earthed"]
[null,null,null,"13- Voltage Ratio ","11/0.416 KV "]
[null,null,null," 14- Type of cooling ","ONAN"]
[null,null,null,"15- Rated power - Continuous","250 kVA "]
[null,null,null,"16- Rated Frequency  ","50Hz"]
[null,null,null,"17- Impedance voltage at 75 deg at nominal tap","≥ 4%"]
[null,null,null,"18- Nominal Voltage of winding             "]
[null,null,null,"A- H.V.   ","11 kV                                                                                     "]
[null,null,null,"B- L.V"," 0.416 kV"]
[null,null,null,"19- Insulation level 11 kV "]
[null,null,null,"A- Lightning Impulse","75 kV"]
[null,null,null,"B- AC power frequency","28 kV"]
[null,null,null,"20- Insulation level LV -phases/neutral AC power frequency","3 kV "]
[null,null,null,"21- Winding temperature rise at rated power","50 C"]
[null,null,null,"22- Top oil temperature rise at rated power                                                    ","45 C"]
[null,null,null,"23- No load loss in ","KW"]
[null,null,null,"24- Load loss at full load at 75 deg temperature ","Kw"]
[null,null,null,"25- Efficiency","≥98.6%"]
[null,null,null,"26- Regulation ","To be filled"]
[null,null,null," 27- Maximum flux density in iron at rated frequency and at rated voltage ratio at nominal voltage","≤ 1.65 Tesla"]
[null,null,null,"28- Maximum current density in windings at\nrated power"]
[null,null,null,"A- H.V. winding","To be filled"]
[null,null,null,"B- L.V. winding","To be filled"]
[null,null,null,"29- No load current at rated voltage                 ","Amp"]
[null,null,null,"30- Material of windings ","Copper"]
[null,null,null,"31- Type of insulation of"]
[null,null,null,"A- Core assembly","To be filled",null,null,null," "]
[null,null,null,"B- Core laminations  \n","To be filled"]
[null,null,null,"32- Thickness of transformer "]
[null,null,null,"A- tank","Minimum 3 mm      "]
[null,null,null,"B-  sides","Minimum 3 mm      "]
[null,null,null,"C- bottom \n","Minimum 3 mm      "]
[null,null,null,"33- Thickness of radiator plates and for cooling tube ","Minimum 1.2 mm      "]
[null,null,null,"34- Winding connection"]
[null,null,null,"A- H.V.","Delta"]
[null,null,null,"B- L.V.\n","Star (Neutral brought out)\n"]
[null,null,null,"35- Vector group symbol ","Dyn11"]
[null,null,null,"36- Tap changer ","Off-load tap changer with 5 positions in the HV winding giving ± 2 x 2.5 %."]
[null,null,null,"37- 11 kV side terminal arrangement","Clamp type for terminating up to 150 mm2 copper conductor"]
[null,null,null,"38- Low voltage terminal arrangement"," Suitable for terminating copper cables of cross section area 6x1x95+1x70 mm2( 1 hole per phase )"]
[null,null,null,"39- Noise level at 0.3 m distance","≤ 55 dB"]
[null,null,null,"40- Transformer oil","To be filled"]
[null,null,null,"A-Type of oil","IEC60296 class 1"]
[null,null,null,"B-Manufacturer","To be filled"]
[null,null,null,"C- Place of manufacture","To be filled"]
[null,null,null,"D-Manufacturer’s type designation ","To be filled"]
[null,null,null,"E-Applied IEC standard","IEC 60296"]
[null,null,null,"F- Kinematic viscosity mm2/s"]
[null,null,null,"F-1/ At 40 deg","≤ 16.5"]
[null,null,null,"F-2/ At -15 deg","≤ 800"]
[null,null,null,"G- Flash point ","≥ 140 C"]
[null,null,null,"H- Pour point","≤ - 30 C"]
[null,null,null,"I- Density at 20 deg C – kg/dm3","≤ 0.895"]
[null,null,null,"J- Breakdown strength","kV"]
[null,null,null,"41- Dimensions of transformer","L 1230 ( mm) x W 700.(mm) x H 1300.(mm)"]
[null,null,null,"42- Weight of transformer ","kg"]
[null,null,null,"43- Type of corrosion protection on steel parts"]
[null,null,null,"A-  Inside tank ","Oil resistant paint"]
[null,null,null,"B- Outside tank ","Metalized, aluminium paint or equivalent"]
[null,null,null,"44- 11 kV bushings"]
[null,null,null,"A-  Name of manufacturer","To be filled"]
[null,null,null,"B-  Make/Brand/Model:","To be filled"]
[null,null,null,"C- Refrence standard","IEC 60137"]
[null,null,null,"D- Type of bushing","To be filled"]
[null,null,null,"E- Rated current","Amp"]
[null,null,null,"F- Rated voltage","KV"]
[null,null,null,"G- Material ","Porcelain "]
[null,null,null,"H- Color ","Brown "]
[null,null,null,"I- Creepage distance","Minimum 300 mm"]
[null,null,null,"45- L V bushings"]
[null,null,null,"A- Name of manufacturer","To be filled"]
[null,null,null,"B- Make/Brand/Model:","To be filled"]
[null,null,null,"C- Reference standard","IEC 60137"]
[null,null,null,"D- Type of bushing"]
[null,null,null,"E- Rated current","Amp"]
[null,null,null,"F- Rated voltage","KV"]
[null,null,null,"G- Material ","Porcelain "]
[null,null,null,"H- Color ","Brown "]
[null,null,null,"I- Creepage distance","mm"]
[null,null,null,"46- Warranty period","One year "]
[null,null,null,"47- Submit manufacturers certification","Yes /required"]
[null,null,null,"48- Submit type test certificates or reports:","Yes /required"]
[null,null,null,"49-  Submit Detail drawings, drawings of HV and LV bushings, details of accessories, brochures and catalogues:","Yes /required"]
[105," Electrical Generator of 150 kVA Capacity",null,"Manufacturer:  ","Original manufacturer (Local Assembled Not acceptable)"]
[null,null,null,"Type:  ","Silent type"]
[null,null,null,"Required Brand: ","Perkins , caterpillar  or equivalent which should be approved by the supervisory committee before starting supplying process"]
[null,null,null,"Engine brand name","To be filed"]
[null,null,null,"Engine model number","To be filed"]
[null,null,null,"Alternator brand name","To be filed"]
[null,null,null,"Alternator model number","To be filed"]
[null,null,null,"Ambient temperature:","Maximum:55/C & Minimum: -10/C     "]
[null,null,null,"Relative Humidity:","Around 60% at maximum temperature  "]
[null,null,null,"Altitude:             ","1000 M above MSL         "]
[null,null,null,"System Voltage:  ","400V/ 3PH, 50 HZ "]
[null,null,null,"Guarantee: ","One year or 1000HR / operation   "]
[null,null,null,"Generator output Range:  ","150 KVA prime  "]
[null,null,null," Exhaust Type: ","Exhaust and inlet/outlet air"]
[null,null,null,"Stand by:  ","Not less 165 KVA, 400A 4pole and 8-hour operation base tank       "]
[null,null,null,"No of cylinders: ","6 inline"]
[null,null,null,"Speed max: ","1500 RPM and Electronic Governor   "]
[null,null,null,"Fuel system: ","Fuel system/storage Diesel tanks"]
[null,null,null,"Battery system: ","Type of starting 24 DC Battery system"]
[null,null,null,"Power factor: ","Between 0.8 and 1   "]
[null,null,null,"Type of excitation: ","Brushless, self-regulation and separately exited"]
[null,null,null,"Cooling type: ","Water cooled  "]
[null,null,null,"No. of cycle: ","Six cycle"]
[null,null,null,"Turbocharged: ","Turbocharged"]
[null,null,null,"Enclosure class: ","Not less than 23  "]
[null,null,null,"Insulation class: ","Class H  "]
[null,null,null,"Earthingstuds: ","Yes/ Required"]
[null,null,null,"Test: ","Yes/Required"]
[null,null,null,"Certificate of origin and inspection documents: ","Yes/ Required"]
[]
[]
[]
[]
[null,null,"Name of Bidder:         ______________________________"]
[]
[null,null,"Authorized signature: ______________________________"]
[]
[null,null,"Functional Title:         ______________________________"]
[]
[null,null,"Company:                   ______________________________"]
[]
[null,null,"Date:                          ______________________________                          "]