REQUEST FOR QUOTATION (RFQ)

(Goods)

| Subject: Procurement, Supply, Installation, Testing and Commissioning of Solar Hot Water System including Solar Pumping System for the cold-water supply to 21 health facilities in Afghanistan | DATE: September 21, 2020 |
| --- | --- |
|  | REFERENCE: UNDP/AFG/2020/RFQ/ 0000007221 |

The United Nations Development Programme (UNDP) hereby invites you to submit a quotation for the Fabrication, Supply, Installations, Testing and Commissioning of Solar Dryers to UNDP Afghanistan.

Full details and specifications are provided in Section 2 of this RFQ.

This RFQ includes the following documents and the General Terms and Conditions of Contract which is inserted in the Bid Data Sheet:

- Letter of Invitation

- Annex 1 - RFQ Bid Data Sheet

- Annex 2 - Technical Specifications

- Annex 3 - Price Schedule

- Annex 4 - General Terms and Conditions

- Annex 5 – Offer Submission Form

- Annex 5 - E-tendering Instructions Manual for Bidders (Attached separately)

- Annex 6 - FAQ for Bidders (Attached separately)

If you are interested in submitting a Quotation in response to this RFQ, please prepare your quotation comprising of all required documents in accordance to Bid Data Sheet and should be submitted through the UNDP ATLAS E-Tendering system, which can be accessed at https://etendering.partneragencies.org.

No hard copy or email submissions will be accepted by UNDP:

The step by step instructions for registration of offerors and quotation/proposal submission through the UNDP ATLAS E-Tendering system is available in the instructions manual for the offerors, attached with this RFQ. Should you require any training on the UNDP ATLAS E-Tendering system or face with any difficulties when registering your company or submitting your bid, please send an email to the E-Tendering Help Desk at procurement.af@undp.org to request for help. The subject of the email should be UNDP/AFG/2020/RFQ/ 0000007221

The offerors are advised to use Internet Explorer (Version 10 or above) browser to avoid any compatibility issues with the E-Tendering system.

Please refer to E-Tendering system for closing date of this RFQ.

Please note that UNDP implements a policy of zero tolerance on proscribed practices, including fraud, corruption, collusion, unethical practices, and obstruction. UNDP is committed to preventing, identifying and addressing all acts of fraud and corrupt practices against UNDP as well as third parties involved in UNDP activities. (See http://www.undp.org/about/transparencydocs/UNDP_Anti_Fraud_Policy_English_FINAL_june_2011.pdf   and  http://www.undp.org/content/undp/en/home/operations/procurement/procurement_protest/ for full description of the policies)

UNDP looks forward to receiving your Quotation and thanks you in advance for your interest in UNDP procurement opportunities.

Goods offered shall be reviewed based on completeness and compliance of the quotation with the minimum specifications described above and any other annexes providing details of UNDP requirements.

The quotation that complies with all of the specifications, requirements and offers the lowest price, as well as all other evaluation criteria indicated, shall be selected.  Any offer that does not meet the requirements shall be rejected.

Any discrepancy between the unit price and the total price (obtained by multiplying the unit price and quantity) shall be re-computed by UNDP.  The unit price shall prevail and the total price shall be corrected.  If the supplier does not accept the final price based on UNDP’s re-computation and correction of errors, its quotation will be rejected.

After UNDP has identified the lowest price offer, UNDP reserves the right to award the contract based only on the prices of the goods in the event that the transportation cost (freight and insurance) is found to be higher than UNDP’s own estimated cost if sourced from its own freight forwarder and insurance provider.

At any time during the validity of the quotation, no price variation due to escalation, inflation, fluctuation in exchange rates, or any other market factors shall be accepted by UNDP after it has received the quotation.   At the time of award of Contract or Purchase Order, UNDP reserves the right to vary (increase or decrease) the quantity of services and/or goods, by up to a maximum fifty per cent (50%) of the total offer, without any change in the unit price or other terms and conditions.

Any Purchase Order that will be issued as a result of this RFQ shall be subject to the General Terms and Conditions attached hereto.  The mere act of submission of a quotation implies that the vendor accepts without question the General Terms and Conditions of UNDP indicated above - http://www.undp.org/content/undp/en/home/procurement/business/how-we-buy.html .

UNDP is not bound to accept any quotation, nor award a contract/Purchase Order, nor be responsible for any costs associated with a Supplier’s preparation and submission of a quotation, regardless of the outcome or the manner of conducting the selection process.

Please be advised that UNDP’s vendor protest procedure is intended to afford an opportunity to appeal for persons or firms not awarded a purchase order or contract in a competitive procurement process.  In the event that you believe you have not been fairly treated, you can find detailed information about vendor protest procedures in the following link:

http://www.undp.org/content/undp/en/home/operations/procurement/protestandsanctions/

UNDP encourages every prospective Vendor to avoid and prevent conflicts of interest, by disclosing to UNDP if you, or any of your affiliates or personnel, were involved in the preparation of the requirements, design, specifications, cost estimates, and other information used in this RFQ.

UNDP implements a zero tolerance on fraud and other proscribed practices, and is committed to identifying and addressing all such acts and practices against UNDP, as well as third parties involved in UNDP activities.  UNDP expects its suppliers to adhere to the UN Supplier Code of Conduct found in this link : http://www.un.org/depts/ptd/pdf/conduct_english.pdf

Thank you and we look forward to receiving your quotation.

Sincerely yours,

Title: Head of Procurement Unit

Date: September 21, 2020

ANNEX 1

Please take note of the following requirements and conditions pertaining to the supply of the abovementioned good/s:

| Delivery Terms [INCOTERMS 2010] (Pls. link this to price schedule) | DAP Kabul for goods to be procured under this contract (Designated locations specified in Annex 2) |
| --- | --- |
| Customs clearance, if needed, shall be done by: | UNDP |
| Exact Address/es of Delivery Location/s (identify all, if multiple) | Designated locations specified in Annex-2 |
| UNDP Preferred Freight Forwarder, if any | N/A |
| Distribution of shipping documents (if using freight forwarder) | N/A |
| Latest Expected Delivery Date and Time (if delivery time exceeds this, quote may be rejected by UNDP) | ☒ 10 weeks |
| Delivery Schedule | ☒Offeror must provide a delivery schedule |
| Packing Requirements | No specific packing requirements, however, the supplier must ensure the goods are delivered to final destination without any physical damage |
| Mode of Transport | Land/Air: The supplier may use any mode of transportation as long as the ordered goods are delivered to final destination as per delivery timeline. |
| Preferred Currency of Quotation | ☒United States Dollars Other currencies shall covert in to United Sates Dollars based on UN operation Exchange rate at time of evaluation; |
| Value Added Tax on Price Quotation | ☒ Must be inclusive of VAT and other applicable indirect taxes |
| After-sales services required | ☒Refer to Terms of Reference for the varying warranty and after-sales requirements. |
| Deadline for the Submission of Quotation | Please refer to E-Tendering system As indicated in the e-Tendering system. Date and Time: As specified in the system (note that the time zone indicated in the system in New York Time zone). PLEASE NOTE: - Date and time visible on the main screen of the event (on the E-Tendering portal) will be final and prevail over any other closing time indicated elsewhere, in case they are different. Please also note that the bid closing time shown in the PDF file generated by the system is not accurate due to a technical glitch that we will resolve soon. The correct bid closing time is as indicated in the E-Tendering portal and system will not accept any bid after that time. It is the responsibility of the bidder to make sure bids are submitted within this deadline. UNDP will not accept any bid that is not submitted directly to the system. Try to submit your bid a day prior or well before the closing time. Do not wait until last minute. If you face any issue submitting your bid at the last minute, UNDP may not be able to assist. |
| All documentations, including catalogs, instructions and operating manuals, shall be in this language | ☒ English |
| Documents to be submitted | ☒Latest Business Registration Certificate; ☒ Company profile; ☒ Duly filled, signed (company stamped) Annex-2 (TCS Form); ☒ Scanned copy of duly filled, signed (company stamped) Annex-3 (Price schedule); ☒ Past contract history including Details of two (2) contracts (paste clients valid reference) for similar requirements (supply delivery, installation and testing of solar powered water heating systems) in the last 3 years, as evidence submit copy of two (2) contracts; ☒ Product catalogs (Mandatory: for all products offered); ☒ Company Bank Statements or audited reports of last two years (2019, 2018) ☒ (only the successful offeror) After-sale security in form of a bank guarantee for the amount of 10% of the contract value, valid until the one-year warranty period |
| Period of Validity of Quotes starting the Submission Date | ☒ 60 days In exceptional circumstances, UNDP may request the Vendor to extend the validity of the Quotation beyond what has been initially indicated in this RFQ. The Proposal shall then confirm the extension in writing, without any modification whatsoever on the Quotation. |
| Partial Quotes | ☒ Not permitted |
| Payment Terms | ☒ 50% upon complete delivery and acceptance of equipment to the locations ☒ 50% upon acceptance, installation, and configuration of the system |
| Liquidated Damages | 0.1% of contract for every day of delay, up to a maximum duration of 1 calendar month. Thereafter, the contract may be terminated |
| Evaluation Criteria | ☒ Technical responsiveness/Full compliance to requirements and lowest price ☒ Full acceptance of the PO/Contract General Terms and Conditions ☒ Financial capacity: The firm should have at-least annual cash flow of $200,000 for last two years. (2018 and 2019 audited report must be submitted to verify firm’s cash flow) ☒Experience: At-least 2 similar projects delivered and successfully completed during last 3 years with one contract amount of at-least $100,000 in similar field including financial clearance ☒ Submission of delivery schedule and Compliance with delivery timeline i.e (10 weeks) ☒ 3 (three) references (name, emails and telephone) which UNDP may contact for reference checks. Alternatively, letter from clients with statements of satisfactory performance are acceptable. |
| UNDP will award to: | ☒ One supplier |
| Type of Contract to be Signed | ☒ Purchase Order / Face sheet contract |
| Special conditions of Contract | ☒ N/A |
| Conditions for Release of Payment | ☒ Written Acceptance of Goods and services based on full compliance with RFQ requirements |
| Annexes to this RFQ | ☒ Specifications of the Goods Required (Annex-1) ☒ Technical Compliance Sheet (Annex 2) ☒ Form for Submitting Supplier’s Quotation (Annex 3) ☒ General Terms and Conditions / Special Conditions (Annex 4) Non-acceptance of the terms of the General Terms and Conditions (GTC) shall be grounds for disqualification from this procurement process. |
| Contact Person for Inquiries (Written inquiries only) | Procurement Unit Procurement.af@undp.org The subject of the email should be UNDP/AFG/2020/RFQ/ 0000007221 Any delay in UNDP’s response shall be not used as a reason for extending the deadline for submission, unless UNDP determines that such an extension is necessary and communicates a new deadline to the Proposers. |

Annex 2- Technical Specifications & Scope of Services – Solar Water Heaters System

- Project Background

The UNDP’s Afghanistan Sustainable Energy for Rural Development (ASERD) project, implemented by the Ministry of Rural Rehabilitation and Development (MRRD) builds on the existing efforts to provide energy to rural areas of Afghanistan. Rural areas of Afghanistan which remains socio-economically underdeveloped in terms of education, incidence of poverty, and access to infrastructure. Lack of access to modern forms of energy has serious health implications on rural Afghani’s and predominantly affects women and children. Lack of access to energy also constrains the productivity of private enterprise and limits delivery of public services. Rural areas of Afghanistan are also blessed with renewable energy resources such as hydro, solar, wind and biomass which, when combined with appropriate technologies and institutional approaches, could significantly support the development of rural areas. The ASERD project is based on four pillars.

- Rural energy services: implement renewable energy projects such as mini-grids powered by small hydro power, solar, wind and thermal energy. In electrified villages opportunities will be provided for local business developers, entrepreneurs and SMEs to take advantage of the availability of power.

- Capacity building and outreach: the energy projects in rural area will also work closely with local MRRD staff and other government entities in order to improve their capacity.

- Innovative models: the program will seek to use and introduce new delivery models to Afghanistan, ranging from technology choice to financial tools.

- Rural Energy policy and Regulation: the program will closely coordinate with stakeholders, especially the Ministry of Energy and Water (MEW) in terms of addressing policy and regulation gaps.

- Context

The Ministry of Rural Rehabilitation and Development (MRRD), with the support of UNDP, aims to support selected health facilities in rural areas of Afghanistan by providing Solar Hot Water System (SHWS) along with the water pumping and storage systems.

Afghanistan has huge solar energy potential, both electrical and thermal. It has over 300 days of sunshine per year with the average solar insolation in between 4 to 6.5 kWh/sq.m/day. Hot water is essential commodity in health facilities however, many clinics in Afghanistan especially in rural areas, do not have access to hot water facilities. This project aims to use the cost effective Standalone Solar Hot Water System (SHWS) for supplying amenity hot water in health facilities for the clinical applications. The MRRD has given preference to maternity clinics while selecting the health facilities.

- Project location

Offeror shall transport and install the solar hot water systems to the following health facilities.

| # | Province Name | District Name | Facility Name | Facility Type |
| --- | --- | --- | --- | --- |
| 1 | Paktya | Dand-wa-Patan | Dande Patan Clinic | Basic Health Center (BHC) |
| 2 | Laghman | Qarghayi | Kanda Clinic | Basic Health Center (BHC) |
| 3 | Kunar | Marah Warah | Marawarah Clinic | Basic Health Center (BHC) |
| 4 | Laghman | Mehtarlam | Alishang Clinic | Basic Health Center (BHC) |
| 5 | Laghman | Mehtarlam | Dewa Clinic | Basic Health Center (BHC) |
| 6 | Khost | Khost (Matoon) | Gharshin Clinic | Basic Health Center (BHC) |
| 7 | Paktya | Gardez | Ibrahim Khel Clinic | Basic Health Center (BHC) |
| 8 | Paktya | Mirzakah | Mirzaka Clinic | Basic Health Center (BHC) |
| 9 | Paktya | Gardez | Mehlan Clinic | Basic Health Center (BHC) |
| 10 | Khost | Tanay | Mirzogai Clinic | Basic Health Center (BHC) |
| 11 | Khost | Shoml | Dowa Menda Clinic | Basic Health Center (BHC) |
| 12 | Khost | Tanay | Khost ARCS Clinic | Basic Health Center (BHC) |
| 13 | Kunar | Khaas Kunar | Mangwal Clinic | Basic Health Center (BHC) |
| 14 | Laghman | Qarghayi | Kashmond Clinic | Basic Health Center (BHC) |
| 15 | Kunar | Asadabad | Nawab Abad Clinic | Basic Health Center (BHC) |
| 16 | Paktya | Jaji | Speenghar Clinic | Basic Health Center (BHC) |
| 17 | Kapisa | Nijrab | Darah-e-Kalan Clinic | Basic Health Center (BHC) |
| 18 | Kapisa | Tagab | Adei zaie Clinic | Basic Health Center (BHC) |
| 19 | Kapisa | Tagab | Payenda Kheil Clinic | Basic Health Center (BHC) |
| 20 | Kapisa | Nijrab | Darah-e-Ghaws Clinic | Basic Health Center (BHC) |
| 21 | Kapisa | Nijrab | Shirwani Clinic | Basic Health Center (BHC) |

- Technical specifications

- Solar Water Heater Assembly

  - Collector Type

Unless otherwise specified, the offeror is required to provide either the Evacuated Tube-Direct Heating Type or the Flat Plate Type Collector Solar Water Heater. Unless otherwise specified, the Solar Water Heater to be considered by the offeror in its offer should have an achievable water temperature of 80 – 150 C. The collector assembly should conform to the concerned standards as specified under the heading of Applicable Standards.

  - Storage

Unless otherwise specified, the size of the Solar Water Heater to be considered by the offeror in its offer is 300L. The storage can either be separate from or incorporated into the main assembly of the collector. These details should be clearly mentioned in the product documentation. The storage assembly should conform to the concerned standards as specified under the heading of Applicable Standards.

  - Transport System

Unless otherwise specified, the offeror is required to provide all the necessary equipment comprising the transport (water supply) system for the facility. These may include, but are not limited to, Piping, Fittings, Valves, Thermostats and Toolkits for O&M purposes. All system components should conform to the concerned standards as specified under the heading of Applicable Standards.

  - System Safety

Unless otherwise specified, the offeror is required to provide ample evidence, in the form of compliance certificates and/or test results, to ascertain the System Safety. The main constituents under this heading are;

- Freeze and Stagnation Protection

- Rust Protection

- Over Temperature Protection

- Pressure resistance

- Reverse Flow Protection

- Safety Valves

- Safety Line and Expansion Lines

- Blow-off Lines

- Lightning Protection

- Water Contamination resistance

The above mentioned system safety aspects should not be deemed to be suffice for overall acceptance of the product offered. The offeror is required to conduct and/or present compliance certificates and test results for all factors outlined in the concerned standards identified in this document.

- Solar Pumping System Assembly

  - Solar PV Panel

Unless otherwise specified, any type of PV module can be offered as long as the module has an overall efficiency of greater than 15%.

The solar PV module should conform to the relevant standards listed under the “Applicable Standards and Certifications” section of these specifications. Moreover, as a general note the solar PV modules should be rugged and have the ability of withstanding extra loads of snow and wind.

  - Mounting Assembly

The mounting assembly used to house the Solar PV module assembly should have the following characteristics;

- Able to withstand high winds

- Corrosion Resistant

- Waterproof Junction Boxes

- Legs that could fix into the ground / roof

It should be noted that these characteristics would be completely at the discretion of the Employer’s Representatives’ approval during site works.

  - Controller and Protection System

The Solar Pumping System should have the controller and all the necessary accompanying systems to ensure the following capabilities;

- Maximum Power Point Tracker (MPPT) to ensure high extraction efficiency from the Solar PV Modules

- A monitoring system to regularly monitor the water level in both the water storage tank and the well and turn On/Off the pump accordingly

A properly sized protection system at the outgoing of the system should be provided to ensure system safety during faults. Further to this, all junction boxes and other housing assemblies should have a protection rating of at least IP 54.

  - Motor/Pump Assembly

Unless otherwise specified, the DC (or AC) Motor/Pump assembly should adhere to the following minimum specifications;

- Type: Submersible / Centrifugal (Preferred); Surface (In some cases)

- Rugged Construction

- Ability to work with a wide range of voltages

- Ability to work for long periods of time, unattended

- Motor/Pump Assembly Efficiency of greater than or equal to 60% at rated head and flow, unless, the specific product for the rated head and flow is not available

- Conformance to relevant standards, as specified under “Applicable Standards and Certifications” section of these specifications

- Shall have power curves clearly showing power consumption at different heads and flow.

- It is preferred that the pump power does not exceed 300 Wp. If this is not the case, the offeror is required to propose the number of required Wp and change the quantity of the required Solar PV Panels (100Wp) in the BoQ accordingly.

  - Inverter

In case, the offeror proposes an AC Pump Assembly, the offeror is required to include an inverter in its offer as well. The inverter should conform to the relevant standards, as specified under “Applicable Standards and Certifications” section of these specifications. The minimum inverter efficiency, as stated in product documentation should be 90%.

- Applicable Standards and Certifications

Unless otherwise specified, the offered product and its components are required to conform to the following list of applicable standards and certifications. It is worth mentioning that any standard and/or certifications complementing any other standard and/or certifications should be mentioned by the offeror.

| Srl. | Standard | Description |
| --- | --- | --- |
| 1 | EN 12975-1:2006 | Thermal Solar Systems and Components – Solar Collectors – Part1: General Requirements |
| 2 | EN 12975-2:2006 | Thermal Solar Systems and Components – Solar Collectors – Part2: Test Methods |
| 3 | ISO 9806: 2013 | Test methods for Solar Collectors |
| 4 | ISO 9459-2:1995 | Solar heating – Domestic water heating systems – Part2: Outdoor test methods for system performance characterization and yearly performance prediction of solar-only systems |
| 5 | ISO 9459-4: 2013 | Solar heating – Domestic water heating systems – Part 4: System performance characterization by means of component tests and computer simulation |
| 6 | ISO 9459-5:2007 | Solar heating – Domestic water heating systems – Part5: System Performance characterization by means of whole system test and computer simulation |
| 7 | ICC-SRCC-OG-100 | Minimum Standards for Solar Thermal Collectors |
| 8 | ICC-SRCC-OG-300 | Minimum Standards for Solar Water Heating Systems |
| 9 | IEC 61215 | Terrestrial photovoltaic (PV) modules |
| 10 | IEC 61730 | Photovoltaic (PV) module safety qualification |
| 11 | IEC 62109-1:2010 | Safety of power converters for use in photovoltaic power systems - Part 1: General requirements |
| 12 | IEC 62109-2:2011 | Safety of power converters for use in photovoltaic power systems - Part 2: Particular requirements for inverters |

Offers for products, including its components, which do not conform to the applicable standards and certifications would not be entertained.

- Labelling

Unless otherwise specified, all the products proposed should have labelling which consist of at least the following product information. This information is of utmost importance d0uring the execution stage of the project.

| SN | Item | Labelling |
| --- | --- | --- |
| 1 | Solar Water Heater Assembly | Name of manufacturer Designation of System Type Serial Number Year of Production Absorber and Aperture area in m2 Nominal Storage in litres Rated Pressure of the drinking water pipe in kPa Heat Transfer Medium Rated Pressure of Heat Transfer Medium |
| 2 | Solar Module Assembly incl. Controller and Protection Assembly | Name of manufacturer Type Serial Number Year of Production Maximum Power, Wpeak Maximum Current, Imax Maximum Voltage, Vmax Short Circuit Current, Isc Open Circuit Voltage, Voc Module operating temperature |
| 3 | Pump/Motor Assembly | Name of manufacturer Type Serial Number Year of Production Maximum head, m or ft Maximum flow, m3/h or gpm or lpm etc Maximum Efficiency Starting Current Normal Operating Conditions (Voltage, Pressure, Temperature) |

- Balance of System

The offeror is required to include all other equipment rendering the system as fit for purpose in its offer, including the cold-water tank. If the existing cold-water tank is not fit for the purpose, offeror shall modify or replace it with a new tank.

- Installation and Commissioning

The offeror is required to provide installation services and provide a system rendered as Fit-for-Purpose. The new hot water system shall be connected to the existing hot and cold plumbing system. In case of absences in the existing piping system to the maternity room and adjacent service rooms whiten the building, the offeror shall install the plumbing and fittings to those rooms for the supply of hot and cold water. During installations, offeror shall do necessary modifications to the roof of the clinics without compromising the insulation of hot water pipes. The offeror shall repair at its own cost any damage caused to the building during installations. The installation would be deemed as fit for purpose after successful commissioning in the presence of Employer’s representative on site.

Unless otherwise specified, each collector, solar PV panel and dc motor/pump assembly should be accompanied with a manufacturer warranty of a minimum of 10, 25 and 2 years, respectively, and the system should be accompanied with 1-year local workmanship warranty. The offeror is expected to bear all costs in case any product requires attention during the workmanship warranty period.

Warranty details:

- Solar Collector – 10 years performance warranty

- Solar PV Panel – 25 years

- DC Motor/Pump Assembly – 2 years

- After Sales Services

Unless otherwise specified, the offeror is required to provide a minimum of 1 year after sales services which include the O&M and repair services.

- Scope of work

The United Nations Development Program (UNDP), Afghanistan has made funds available for engaging a capable and qualified Afghan Contractor to carry out procurement, supply, installations, configuration,  testing,  commission and one-year guarantee of Solar Hot Water Systems (SHWS) to the qualities stipulated in the ‘Bill of Quantities’ to selected health facilities in Afghanistan. The detail scope of work includes:

- Verification of sites parameters: UNDP will provide initial lists of health facilities. The offeror must visit the sites and verifies the site parameters before procurement of solar hot water system equipment. Some health facilities may require modification of the existing cold-water tank or the extension of plumbing system. The offeror must verify them during the site visit and include them in the cost.

- Procurement and supply: In accordance with the provided technical specification, offerors shall procure and supply components of the solar hot water systems.   All components of the system must be made available to the Employer or its representative for inspection and quality assurance in Kabul before their transportation to the locations for installations. Any units that fails the quality inspection against the technical specification must be replaced.

- Transportation, Installations and Calibrations: The offeror shall transport hot water system components to the locations stipulated in this bid document. The offeror must repair or replace any damage to components occurred during the transportation. The offeror shall install, assemble and calibrate the components and ensure their functionality and specified output quantities.

- Users’ training: The offeror shall provide trainings about the use of the solar hot water system to the users. At the end of training, users must be able to understand at least the following activities about the usage of dryer.

- Function of each components

- Users safety

- Minimum requirements for the operation of the system e.g. minimum water level in solar collector

- Preventive maintenance of the components

- Troubleshooting problems

Annex – 3 FORM FOR SUBMITTING SUPPLIER’S  QUOTATION

We, the undersigned, hereby accept in full the UNDP General Terms and Conditions, and hereby offer to supply the items listed below in conformity with the specification and requirements of UNDP as per RFQ Reference No. UNDP/AFG/RFQ/2020/:0000007221

Table 1:

| Item | Description | Qty | Unit of Measure | Unit Price | Amount |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | USD | USD |
| 1 | Solar Water Heater Assembly incl. mounting assembly, valves etc. and all other auxiliary equipment rendering the system Fit-for-Purpose | 21 | units |  |  |
| 2 | Solar Water Pump, Submersible or surface as per the site condition, operating at approx. TDH=40 m and flow rate=0.30 m3/h and a Maximum Power Input = 250W incl. Controller, Junction Boxes, Protection Gear, Grounding Rod, Cabling and all other equipment rendering the system Fit-for-Purpose | 21 | units |  |  |
| 3 | Solar Photovoltaics models, 125 Wp each including mounting assembly, cables and sockets | 63 | units |  |  |
| 4 | Solar Invertor, 300 Wp, including cables and accessories, compatible to the solar water pump using electricity from the solar modules | 21 | units |  |  |
| 5 | Installation, configuration and testing, commissioning and users’ training | 1 | LS |  |  |
| 7 | One-year warranty and after sales services | 1 | LS |  |  |
| 8 | Any other costs (Please specify) |  |  |  |  |
| TOTAL (DAP) |  |

Implementation Schedule

All implementation activities must be completed within 10 weeks from the date of signing the contract. . Offerors shall provide a delivery schedule in alignment with the given date.

[Enter name of authorized staff]

[Designation]			[Click here to enter a date]

TABLE 2 : Offer to Comply with Other Conditions and Related Requirements

| Other Information pertaining to our Quotation are as follows : | Your Responses |
| --- | --- |
|  | Yes, we will comply | No, we cannot comply | If you cannot comply, pls. indicate counter proposal |
| Delivery Lead Time of 10 weeks |  |  |  |
| Compliance & acceptance of Scope of Services as identified in Annex 2 (Specifications/TOR) |  |  |  |
| Product catalogs provided for all products offered |  |  |  |
| Financial capacity: The firm should have at-least annual cash flow of $200,000 for last two years. (2018 and 2019 audited report must be submitted to verify firm’s cash flow) |  |  |  |
| Experience: At-least 2 similar projects delivered and successfully completed during last 3 years with one contract amount of at-least $100,000 in similar field including financial clearance |  |  |  |
| Warranty and After-Sales Requirements |  |  |  |
| Training on Operations and Maintenance |  |  |  |
| Minimum one (1) year warranty on both parts and labor |  |  |  |
| Service Unit to be Provided when the Purchased Unit is Under Repair |  |  |  |
| Brand new replacement if Purchased Unit is beyond repair |  |  |  |
| Others |  |  |  |
| Validity of Quotation for period of 60 days |  |  |  |
| All Provisions of the UNDP General Terms and Conditions |  |  |  |

All other information that we have not provided automatically implies our full compliance with the requirements, terms and conditions of the RFQ.

[Name and Signature of the Supplier’s Authorized Person]

[Designation]

[Date]

Annex 4- General Terms and Conditions

http://www.undp.org/content/dam/undp/library/corporate/Procurement/english/3.%20UNDP%20GTCs%20for%20Contracts%20(Goods%20and-or%20Services)%20-%20Sept%202017.pdf

ANNEX 5 - OFFER SUBMISSION FORM

Must be duly completed and stamped by the Offeror and returned with the Offer.

To:	United Nations Development Programme

Dear Sir/Madam,

We, the undersigned, hereby offer to supply the goods and related services in accordance with your Request for Offer (Ref: ……)  dated      . We are hereby submitting our offer, which includes the Price Schedule (annex 1).

We hereby declare that:

- All the information and statements made in this Offer are true and we accept that any misrepresentation contained in it may lead to our disqualification;

- We are currently not on the removed or suspended vendor list of the UN or other such lists of other UN agencies, nor are we associated with, any company or individual appearing on the 1267/1989 list of the UN Security Council;

- We have no outstanding bankruptcy or pending litigation or any legal action that could impair our operation as a going concern; and

- We do not employ, nor anticipate employing, any person who is or was recently employed by the UN or UNDP.

We confirm that we have read, understood and hereby fully accept the Schedule of Requirements and Technical Specifications describing the duties and responsibilities required of us in this RFO, and the General Terms and Conditions of UNDP’s Standard Contract for this RFO.

We agree to abide by this Offer for 60 days.

We undertake, if our Offer is accepted, to initiate the supply of goods and provision of related services not later than the date indicated in the Data Sheet.

We fully understand and recognize that UNDP is not bound to accept this Offer, that we shall bear all costs associated with its preparation and submission, and that UNDP will in no case be responsible or liable for those costs, regardless of the conduct or outcome of the evaluation.

Name of the Offeror: 	________________________________________________

Address of the Offeror:	________________________________________________

Authorized signature: 	________________________________________________

Name of authorized signatory:	________________________________________________

Functional Title:	________________________________________________

Email address:	________________________________________________

Date:	________________________________________________