## Grand total Final
GRAND SUMMARY Phase 2
PART | DESCRIPTION
II | Priority 1 - Package | 0
1 | HVAC system & Related Works | 0
2 | Finishes Works | 0
3 | Tiling Works | 0
II | Priority 2 - Package | 0
1 | Outside Works | 0
Rehabilitate Stone Facades
New cladding for basement Façades (Wet Fixation)
Stamped Concrete
III | Security Package | 0
1 | Electrical Works | 0
| TOTAL SUMMARY (VAT Excuded) | 0
Discount (%)
| GRAND TOTAL SUMMARY (VAT Excuded) | 0
| * All prices are subject to be increase by 22%, according to the local market and the economic conditions in Lebanon. | 0
Cost Highlighted in yellow are previously priced by the contractor in phase 1

## Priority 1
Item No. | Description | Unit | Qty | Unit Price US.$. | Total Price US.$.
I | Priority 1 - Package
1 | HVAC system & Related Works
HVAC system (heating ventilation and air conditioning)
1.1 | VRF Intdoor Fan Coil Units
Supply, Install and Test Fan Coil Units Complete with all Wiring, Valves, Strainers, Filters, Plenum Box, valves, Acoustic Attenuation Treatments, internal lining, Control Panel, Circuit Breaker, Thermostat, Condensate drain, Copper Pipes etc.. all Necessary Insulation and Accessories, as Specified.
a | Ceiling Concealed Type [2.8kw] | No | 1 |  | 0
b | Ceiling Concealed Type [3.6kw] | No | 8 |  | 0
c | Ceiling Concealed Type [4.5kw] | No | 8 |  | 0
d | Ceiling Concealed Type [5.6kw] | No | 17 |  | 0
e | Ceiling Concealed Type [7.1kw] | No | 1 |  | 0
f | Ceiling Concealed Type [9kw] | No | 6 |  | 0
g | Ceiling Concealed Type [11.2kw] | No | 9 |  | 0
h | Ceiling Concealed Type [14kw] | No | 1 |  | 0
i | Wall Mounted Type [4.5kw] | No | 2 |  | 0
j | Wall Mounted Type [7.1kw] | No | 1 |  | 0
1.2 | VRF Outdoor Units
Supply, Install and Test VRF Units Complete with all Wiring, Valves, Copper Pipes etc.. all Necessary Insulation and Accessories, as Specified.
a | ACU-B [50.4kw] | No | 1 |  | 0
b | ACU-1F [67.4kw] | No | 1 |  | 0
c | ACU-2F [73.5kw] | No | 1 |  | 0
d | ACU-3F [123.5kw] | No | 1 |  | 0
1.3 | Fans
Supply, Install and Test the Following Fans, Including Flanges, Support Framing, Mounting Bolts, Controls, Sound Attenuators if Required and all Necessary Fixing Accessories and Connection as Specified:
Exhaust Fans
a | Type EF-B1, 640 L/S, 1/3 HP | No | 1 |  | 0
1.4 | Ductwork
a | Galvanized steel ducting for air/conditioning and ventilation system low velocity including all beads, junctions, fittings, reducers, accessories, fire dampers, volume dampers, interior lining splitter dampers, supports, and flexible joints including those not shown on drawings, as specified and as shown on drawings. | Kg. | 4300 |  | 0
b | Insulation for indoor ductwork as specified. | m2 | 595 |  | 0
1.5 | Air Outlets
Supply and Fix the Following Complete with all Duct Connections and Framing as Specified and as Shown on Drawings (finish paint color as per architect):
1.5.1 | Supply ceiling diffuser (SCD)
a | 300x300mm | No | 14 |  | 0
b | 380x380mm | No | 18 |  | 0
1.5.2 | Return ceiling diffuser (RCD)
a | 300x300mm | No | 11 |  | 0
b | 380x380mm | No | 17 |  | 0
1.5.3 | Exhaust ceiling diffuser (ECD)
a | 225x225mm | No | 2 |  | 0
1.5.4 | Supply air register (SAR)
a | 450x200mm | No | 1 |  | 0
b | 600x200mm | No | 1 |  | 0
c | 650x150mm | No | 10 |  | 0
d | 850x150mm | No | 24 |  | 0
e | 1200x200mm | No | 1 |  | 0
1.5.4 | Return air register (RAR)
a | 450x200mm | No | 1 |  | 0
b | 600x200mm | No | 1 |  | 0
c | 650x150mm | No | 10 |  | 0
d | 850x150mm | No | 24 |  | 0
e | 1200x200mm | No | 1 |  | 0
1.5.5 | Exhaust air register (EAR)
a | 200x100mm | No | 14 |  | 0
b | 250x100mm | No | 1 |  | 0
1.6 | Volume Dampers | Item | 1 |  | 0
1.7 | Condensate drain pipes Complete with Insulation as Specified:
a | 25mm | m | 215 |  | 0
b | 32mm | m | 75 |  | 0
1.8 | Electrical Works
1.8.1 | Panel Boards
Supply, install and connect electrical panel boards including cabinets, circuit breakers, busbars, connectors, switch-disconnectors, spares and spaces including all trunking and wires, ground conductors and accessories from SDB's to branches circuit breakers as shown and specified on drawings. All circuit breakers shall be labeled and identified with a durable fixed identification with label support sheet mounted in a type written circuit directory. - The cable glands shall be provided at the termination of all cables rigid PVC conduits at the enclosure of the panel board's. - The outgoing branches feeders are connected to circuit breakers by insulated flexible wires, running in PVC trunks (with 50% space) and suitable insulated connectors, mounted at the panel bottom. - Secondary panel boards have to be provided with engraved metal nameplate mounted with resistant corrosion screws. - The panel boards have to be assembled for a perfect operation and to the satisfaction of the engineer.
NB: The IP shall be 43 unless otherwise indicated. The ratings and the breaking capacities shall be as noted and satisfying the IEC 947-2. The equipment shall be from SCHNEIDER, or approved equal.
a | PB-HVAC | Unit | 1 |  | 0
1.8.2 | Feeder Cables
Supply, install and connect, Cu/PVC/PVC cables, including junction boxes, cable trays, cable cleats, cable glands, sealing compound, cable sleeves and all necessary accessories including conduits and liquitight flexible conduits (for outdoor and wet areas) where necessary, as specified and shown on drawings and to the satisfaction of the engineer. - Supply, install and connect Cu/PVC 600 Volts, earth cables (to IEC 502) including accessories as specified and to the satisfaction of the Engineer. - The electrical cables (35mm2 and above), have to be fixed to cable trays and metallic supports on shafts by a metallic clamps. - The single core cables have to be installed in trefoil arrangement. - The electrical cables on cables tray, ladders and in shafts have to be spaced by at least one diameter (of the Biggest size).
1.8.2.1 | Cables Cu/PVC/PVC 500/1000 V, to IEC 502.
a | CABLE 4x70+35mm2 | m | 120 |  | 0
b | CABLE 3x25+16mm2 +E=16mm2 | m | 55 |  | 0
c | CABLE 3x10+10mm2 +E=10mm2) | m | 155 |  | 0
Note: The exact distance to be remeasured on the site.
1.8.3 | Cable Trays
Supply, install and connect the following cable trays, hot dip galvanized after perforation and bending, rolled flangers, 4.8cm flange height, 1.5mm minimum thickness, as shown on the drawings, including : - 3 way or two way derivations, elbows, supports, etc… and all the connections, supports and necessary accessories, all hot dip galvanized. - Covers where needed, having the same specifications as the cable trays.
a | 150mm cable tray with cover, for incoming feeders exact distance to be remeasured on site | m | 110 |  | 0
b | 200mm HDG cable tray for feeders up to roof | m | 53 |  | 0
1.8.4 | Disconnect Switches and Electrical Outlets
Supply, install and connect the following disconnect switch complete including outlet box, cabling/conduit works back to respective panel boards,with all related accessories as shown on drawings and as specified, ABB, Schneider or approved equal. Note:Disconnect switches with wiring size 4 mm2 or less shall be priced with wiring included.
1.8.4.1 | Disconnect Switches
a | Single phase disconnecting switch weather proof 3x16A IP54 For FCU and EF | Unit | 55 |  | 0
b | Three phase disconnecting switch weather proof IP67 For ACU 4x100A | Unit | 1 |  | 0
c | Three phase disconnecting switch weather proof IP67 For ACU 4x63A | Unit | 2 |  | 0
d | Three phase disconnecting switch weather proof IP67 For ACU 4x40A | Unit | 1 |  | 0
1.8.4.2 | Electric Outlets
a | Single Outlet for FCU with wiring | Unit | 55 |  | 0
b | Empty conduit for Thermostate | Unit | 54 |  | 0
1.9 | False Ceiling Works
a | New Gypsum Board Suspended Ceiling (60x60cm) | m2 | 845 |  | 0
Supply and install gypsum board tiles suspended ceiling 60 x 60 cm Work to include: - Remove old existing ceiling and all above damaged and unused items that may affect the safety and the installation of the new suspended ceiling. - Labors - Materials - Accessories - Angles - Plywood - All needed items as per the Engineer instructions
أسقف مستعارة من مربعات الجفصين (60x60cm): توريد وتركيب أسقف مستعارة من مربعات الجفصيل الجاهزة قياس 60*60 سنتم وتشمل الأشغال : - إزالة الاسقف الموجودة والتالفة وكل ما وجد اعلى السقف المستعار من بنود تالفة ومتضررة وقد تسبب خطر على السلامة وعلى تركيب السقف المستعار الجديد. -المواد والإكسسوارات ونظام التعليق القابل للتعيير للحصول على مستويات متناسقة وبدون أي إنحراف أو تموجات. -الزوايا التي ستوضع على الجدران -قضبان الألومنيوم الفاصلة وتكون على شكل T مقلوبة -ألواحد خشبية اللازمة لتحديد شكل السقف بالشكل النهائي -سقالات ويد عاملة -وكل ما يلزم لإنهاء الأشغال حسب المواصفات وتعليمات الجهة المشرفة.
| HVAC system and related Works TOTAL CARRIED TO PRICE SUMMARY |  |  |  | 0
2 | Finishes Works
2.1 | Internal Paint
a | Repair of Existing Plaster | m2 | 650 |  | 0
Rehabilitate and repair cracked and damaged plaster indoor & outdoor Works to include: - Determine the location and remove all loose items around the area - Remove the cracked plaster layer - Install galvanized steel mesh - Clean the places with suitable materials - Fill all cracks after widening (10 cm or as per engineer instruction) by tinocrete or equivalent - Apply the finish rough plaster layer - Apply the second smooth plaster layer - Labor - Material & Scaffolding - All needed items as per drawings and the Engineer instructions
أعمال ترميم ورقة موجودة إسمنتية: ترميم ومعالجة الورقة الإسمنتية الداخلية وخارجية بما فيها الشقوق والتشققات ... إلخ وتشمل الأعمال: -تحديد الأماكن المراد إصلاحها ومعالجتها. -نزع الورقة الإسمنتية الغير فنية والغير سليمة. -توسعة الشروخ بحدود 10 سنتم على كامل إتجاه الشرخ -تركيب شبك معدني غير قابل للصدأ -تنظيف مكان الأعمال بالمواد اللازمة -تعبئة الشروخ بمادة Tinocrete أو ما يعادلها -طبقة رشة مسمارية إسمنتية -طبقة إسمنتية خشنة -طبقة إسمنتية ملساء -اليد العاملة والسقالات والمعدات والمواد - كل ما يلزم لإنهاء الأشغال حسب المواصفات وتعليمات الجهة المشرفة.
b | Internal Paint (walls & ceiling) | m2 | 11670 |  | 0
Unleaded paint acrylic. Works shall include the following: - Remove all paint on elements by using paint removal and burning specially for the oily paint. - Putty - Apply base layers - Apply three layers of wheel for Acrylic paints (super tuber paint), The applicant time between each layer should be 24 hours. - Color and kind of paint to be determined by the Engineer on site in addition to the mode of roller wheel. Work to include all necessary items tools stairs and any temporary steel structure to reach all locations - Labor - Material & Scaffolding - All needed items as per drawings and the Engineer instructions
الدهان الداخلي : تقديم وطلاء رولو اكريليك سوبر كاوتشوك خالي من الرصاص باب أول. وتشمل الأعمال: - قشر الدهان القديم وحفه ويتم تنظيف الجدران والأسقف من الرواسب والغبار. - معجونة - طبقة اساس - 3 طبقات من أكريليك سوبر كاوتشوك تباعاً (كل 24 ساعة طبقة) - على أن يتم تحديد الللون ونقشه بالرولو بموافقة المهندس المشرف مع كل ما يلزم من مواد ومقتضيات ويد عاملة وسقالات لإتمام العمل على أكمل وجه.
2.2 | Rehabilitate the existing Wooden Doors | m2 | 165 |  | 0
Rehabilitate the existing timber openings & timber doors for any existing dimension. Work to include: - The frame and the architrave - Replace all broken items and replace it with new, same shape, material and workmanship. - Remove all existing paint - Apply anti insects layer - Apply putty - Apply one layer undercoat - Apply three layers of epoxy paint for internal use - Replace all Hinges, locks (cylinder lock), and handles. - Replace the broken and unclean glass. - Labors - All needed items as per the Engineer instructions
أشغال ترميم خشبية داخلية : ترميم وتاهيل أبواب ( باب + صندوق + حواجب) داخلية مهما كان قياس الفتحة وعرض الصندوق والحواجب وتشمل الأشغال: - تحديد أماكن المتضررة والعمل على نزعها حسب أصول المهنة (درفة أو صندوق او حاجب) مع المحافظة على نفس نوعية الشكل الموجود. - نزع جميع القطع الغير صالحة والتي تعرضت للتلف أو التسوس أو الكسر أو الثقوب مهما كانت درجة الضرر الذي أصابها. مع المحافظة على نفس نوعية الشكل الموجود. - تركيب القطع بواسطة الفرز واللسان ما بين الموجود والجديد على أن تكون الأخشاب المستخدمة مماثلة للموجود. - دهان خاص لحماية الخشب من التسوس. - حف وإزالة الدهان بالكامل مع إستعمال مواد مزيلة للدهان - أساس أندركوت زيتي وجه واحد - طلس معجونة وجيهن - ثلاث أوجه بويا - تغيير جميع الغالات والمفصلات والمسكات (cylinder lock) على ان تكون صناعة أوروبية - إستبدال زجاج مكسور أو مغطى بالدهان بآخر مماثل للموجود - اليد العاملة - كل ما يلزم لإنهاء الأشغال حسب المواصفات وتعليمات الجهة المشرفة.
2.3 | New Timber Doors at Director zone: Supply and install flush timber door with wooden veneer facing and the door should have 10cm width frame between the plywood and fill with timber beads by tongue and grow each 5cm, and the door edges should behead wood and fixed by tongue. With wireless key lock All works should be done as per the Engineer instructions | m2 | 18 |  | 0
أبواب خشبية داخلية جديدة في قسم المدير: تقديم وتركيب باب كامل خشب معاكس للباب تجليد قشرة خشبية حسب المواصفات المطلوبة مؤلف من برواز خشب زان بعرض 10سم مركب بالفرز واللسان وتقاطيع داخلية من خشب الشوح الجيد قياس 3.5*8سم كل 25سم عرضاً، و 3.5*3.5 سم كل 5سم طولاً، مغطى على الوجهين بخشب معاكس باب أول سماكة 6ملم تجليد قشرة خشبية على الجهتين ينزل بفرز. (مع قفل لاسلكي) - كل ما يلزم لإنهاء هذه الأشغال حسب المواصفات الفنية وتعليمات المهندس المشرف.
2.4 | Signage Labelling | No. | 30 |  | 0
Supply and install rooms and toilets wooden name boards. Work to include: - All necessary fixations - Labors - List will be provided by the administration prior to the commencement of work. - All needed items as instructed by the engineer.
لوحات أسماء الغرف: تقديم وتركيب لوحات أسماء الغرف والحمامات من الخشب. تتضمن الأعمال: - التثبيت - اليد العاملة - لائحة اسماء الغرف تقدم من قبل ادارة المبنى قبل البدء بالاعمال. - كل ما يلزم لإنهاء هذه الأشغال حسب المواصفات الفنية وتعليمات المهندس المشرف.
2.5 | Automatic Soap Dispenser Supply and install ABS and Aluminum soap dispenser wall type fixation. - Hands free operation. - Battery operated All works should be done as the Engineer instructions | No. | 17 |  | 0
2.6 | New Timber Cabinets under toilet counter top: Supply and install wood cabinets under toilet counters. Work to include: - Use melamine wood (Hydrofuge) - Supply all needed accessories - Labors & materials - All needed items as per the Engineer instructions | lm | 22 |  | 0
2.7 | Makeover of Kitchen Hall Entrance: General makeover for the kitchen entrace door works to includes: - Demolishing of existing counter top and wall tiles and remove debris. - New plaster works. - New paint work. - Supply and install new granite counter top (310x60cm). - Use melamine wood (Hydrofuge) for shelves under the counter. - Supply all needed accessories - Labors & materials - All needed items as per the Engineer instructions | LS | 1 |  | 0
| Finishes Works TOTAL CARRIED TO PRICE SUMMARY |  |  |  | 0
3 | Tiling Works
3.1 | Remove Existing Floor Tiles And Replace it with new ceramic Tiles (60x60cm minimum)
Remove existing any type of flooring and install new as per specifications. Work to include: - Materials - Suitable material for filling - Labor - Cutting and repair - Lining - Rubbing / Cleaning - All needed items as per the Engineer instructions
إزالة أرضيات بلاط موجود وتركيب بلاط سيراميك جديد (60x60cm minimum) نزع أرضيات موجودة من أي نوع كانت وتركيب بلاط جديد - المواد - سرك - اليد العاملة ذات خبرة في هذا الإختصاص - القص والإزالة مع ترحيل الناتج إلى خارج الموقع والقطع والتركيب - المونة اللاصقة - الروبة النهائية - جلي / تنظيف - كل ما يلزم لإنهاء الأشغال حسب المواصفات وتعليمات الجهة المشرفة.
a | Third Floor | m2 | 680 |  | 0
b | Second Floor | m2 | 470 |  | 0
c | First Floor | m2 | 440 |  | 0
d | Ground Floor | m2 | 175 |  | 0
e | Basement Floor | m2 | 1050 |  | 0
f | Library - Conference Room - Educational Center | m2 | 200 |  | 0
| Tiling Works TOTAL CARRIED TO PRICE SUMMARY |  |  |  | 0

## Priority 2
Item No. | Description | Unit | Qty | Unit Price US.$. | Total Price US.$.
II | Priority 2 - Package
1 | Outside Works
1.1 | Landscaping works
Agricultural Works: Rehabilitate all flowers beds and remove all harmful plants and prun of all trees in addition to the supply of proper aggregation soil to the flower beds for their healthy form. As per specifications and as per the Engineer instructions
الأعمال الزراعية: أعمال التسوية لأحواض الأشجار الموجودة وتنظبفها من الأعشاب الضارة وتشحيل الأشجار وتوريد التربة الزراعية الصالحة والسماد الكافي مع توريد وإستكمال أشغال أحواض مماثلة لما هو موجود لتأتي الأشغال وحدة متناسبة بالشكل مع زراعة الأشجار حسب المواصفات وتعليمات الجهة المشرفة.
a | Planting | m2 | 185 |  | 0
Supply and install new plants, works to include: - Place the plant (Flowers and bushes) - Provide proper care for the planted area - Agricultural soil - Labors - Materials / Tools - All needed work as per the Engineer instructions
الأعمال الزراعية الجديدة: تقديم وزراعة شتول جديدة (زهور وشجيرات) تشمل الأشغال: - تحديد الأماكن المراد زراعتها. - تراب زراعي صالح مع السماد اللازم. - الريّ مع الإعتناء بالأشجار. - اليد العاملة. - المواد / المعدات - كل ما يلزم لإنهاء الأشغال حسب المواصفات وتعليمات الجهة المشرفة.
b | Grass | m2 | 185 |  | 0
Supply and install natural grass carpets and the work includes: - Clear the location to a depth of 25 cm - Place proper soil for the grass carpet - Install the grass carpet - Irrigation - Labors - Materials / Tools - All needed work as per the Engineer instructions
زراعة عشب طبيعي: توريد وتنفيذ حصائر عشبية طبيعية لزوم بعض الأماكن الخارجية. تشمل الأشغال: - تنظيف الأماكن المراد زراعتها من كل الشوائب الموجودة والأعشاب وحرث الأرض مع إزالة الطبقة الغير صالحة للإستخدام وذلك بعمق لا يقل عن (25سم) مع الأخذ بعين الإعتبار الميول المناسب للموقع. - توريد ووضع تراب زراعي صالح مع السماد اللازم. - توريد وفلش الحصائر العشبية الطبيعية مع الإعتناء بها. - الريّ حسب الحاجة. - المواد والمعدات واليد العاملة. - كل ما يلزم لإنهاء الأشغال حسب المواصفات وتعلميات الجهة المشرفة.
c | Irrigation System: Supply, install and test, irrigation network along with all related accessories (pipes, sprinklers, bubblers, mini-sprinklers, etc…) | Item | 1 |  | 0
1.2 | Outside wall Paint and cladding
a | Rehabilitate Stone Facades | m2 | 375 |  | 0
Rehabilitate works on natural stone facades Work to include: - Determine the location of the damaged stone walls and location of dampness - Treat the dampness and the causes - Repair the stone by renewing the damaged and replace it with new ones with same stone - Clean the stones by sand. - Clear the place and infill in between the coarse (Lining) - Labors - Materials - All needed work as per the Engineer instructions
أشغال الحجر: أشغال ترميم واجهات من الحجر الصخري: إعادة نهو خارجي للواجهات المحددة على المخططات الخارجية وتشمل الأشغال: - السقالات واليد العاملة والمعدات والتنظيف. - الكشف على أماكن الأشغال. - معالجة النش ومسبباته. - ترميم الحجر وفقاً للمخططات المرفقة مع الإلتزام التام بما ورد في دفتر المواصفات والأحجار المستخدمة مماثلة للموجود من حيث الشكل واللون. - تنظيف الحجر بواسطة ضرب الرمل النظيف والخالي من الملونات. - تكحيل الحجر مماثل للموجود. - اليد العاملة - المواد. - كل ما يلزم لإنهاء الأشغال حسب المواصفات وتعلميات الجهة المشرفة.
b | New cladding for basement Façades (Wet Fixation) | m2 | 185 |  | 0
Supply and install new ceramic tile on basement facades Works to include: - Removing existing tiles - Ceramic Tiles Average size 120x60cm Thick: 2cm (Only grade A imported ceramic tiles European origin or equivalent shall be used). - Scaffolding - Labors - Mortar - Complete shop drawings should be submitted for approval - All needed items as per the Engineer instructions
أعمال بلاط للواجهات الخارجية: توريد وتركيب بلاط للواجهات الخارجية وتشمل الأشغال: - إزالة البلاط الموجود - بلاط من نوع سيراميك حجم إجمالي 120x60سم سماكة 2سم (على ان يكون البلاط من الدرجة الأولى أوروبي المنشأ أو ما يعادله) - السقالات - اليد العاملة - المونة - تقديم المخططات التنفيذية والحصول على موافقة الجهة المشرفة قبل البدء بأعمال التنفيذ - كل ما يلزم لإنهاء الأشغال حسب المواصفات وتعليمات الجهة المشرفة.
1.3 | Stamped Concrete | m2 | 255 |  | 0
Supply and cast stamped concrete for parking area after complete leveling of the surfaces by fitting them with suitable material before placing the steel reinforcement The Contractor should submit shop drawings for the works (showing all necessary details levels, steel bars diameter & spacing including the slop ≥ 1% ) Work to include: - Materials - Steel reinforcement - Concrete - Curing - Construction joints - Making the surface suitable - Labors - Finishing works (slab should be sealed with 2 coats) - All needed work as per the Engineer instructions
أعمال باطون مطبع: تنفيذ وعمل أرضية خرسانية مطبعة (Stamped Concrete) لزوم موقف سيارات بعد تسوية الأرضية ومعالجة الأخاديد والفجوات بواسطة الدمك بمواد صالحة. على المقاول تقديم خرائط تنفيذية للاعمال (تظهر كل التفاصيل اللازمة من شقلات وقطر حديد التسليح والمسافات مع منسوب الميول ≥ 1% ) وتشمل الأعمال: - المواد والمعدات المستخدمة. - حديد التسليح اللازم إنفاذاً لمخططات Shop Drawing. - فواصل إنشائية لازمة. - تخشين وجه الأرضية. - السقي. - اليد العاملة. - النهو الأخير (النقشة) يتم إختيارها طبقاً لتوجيهات الجهة المشرفة. - طبقتين من السيلر. - كل ما يلزم لإنهاء الأشغال حسب المواصفات وتعليمات الجهة المشرفة.
| Outside Works TOTAL CARRIED TO PRICE SUMMARY |  |  |  | 0

## Security
Item No. | Description | Unit | Qty | Unit Price US.$. | Total Price US.$.
III | Security Package
1 | Electrical Works
A.1 | External Lighting Flood Lights | No | 24 |  | 0
Supply, install, test and commission External Lighting Flood Lights 100W, IP65 and all accessories with Solar panels (Eff. 14% minimum) IP65, fuses plates, CB's , XLPE wiring, Batteries and Battery charger (Inverter) with related enclosure IP65. Complete with all required connections , fixation items, earthing and wiring ready for use as per drawings and specifications. All items shall be of european origin (except batteries shall be Japanese) autonomy at least 8 hours. - Labors - Materials - All needed work as per the Engineer instructions Motion-activated LED flood lights
A.2 | First Aid Box | No | 7 |  | 0
Supply, install, Wood Box With Glass Door Leaf to maintain First - aid kit with dimension 30cmx30cmx17cm(Depth) - Labors - Materials - All needed work as per the Engineer instructions
A.3 | Steel Lockers For Guard Room | No | 6 |  | 0
Two Metal lockers double decker 450mmx300mmx800mm (DepthxWxH), 1mm steel thick - 2 points latching per door - Louvers on door for ventilation - Vertical door flange, door hinge welded to frame. - Locker element fixed to the wall by screws. - Built-in locks. - Provide two keys for each lock, & two master keys for the system. Works to include: - Materials & Labors - Transportation and installation on site - All needed accessories (European origin) - All needed items as per site engineer instructions - Color selection shall be as per site engineer approval. - All needed work as per the Engineer instructions
خزانة حديد طيقتين فوق بعضهما عرض 300 ملم عمق 450 ملم وعلو 800 ملم، سماكة الحديد 1 ملم. نقطتين إرتكاز لكل درفة - فتحات تهوئة لكل درفة - فلنجات الدرف عامودية والمفصلات تلحم إلى الإطار - تثبت الخزانة إلى الحائط ببراغي - قفل مدموج - تأمين مفتاحين لكل قفل خزانة وكذلك تسليم مفتاحين رئيسيين لجميع أقفال الخزانات. وتشمل الأعمال: - المواد واليد العاملة - النقل والتركيب في الموقع - الأكسسوارات (أوروبية الصنع) - وكل ما يلزم لإنهاء هذا الاشغال حسب المواصفات الفنية وتعليمات الجهة المشرفة. - يتم اختيارالألوان بحسب تعليمات المهندس المشرف.
| Outside Works TOTAL CARRIED TO PRICE SUMMARY |  |  |  | 0