## Sheet1
UNDP-RFQ-2020-342:Specifications for 10 KW Solar System at District Courts
North Waziristan, Bajaur & Mohmand
Fixed Cost
S # | Description | Qty | Unit price in PKR | Total Amount in PKR
1 | Min 400 Watt or above - Solar Panels (PV modules) mono-crystalline, IEC Certified A Grade, TUV 61215, TUV 61730 , | 26 |  | 0
Year of manufacturing (Important) Format like DD:MM:YYYY to be laminated inside the module. (should be not older than 1 year), PV Module Minimum Efficiency 17.5% or above.
Total Watts = Min 400x26 = 10,400 Watt
Warranty: 25 Years Performance warranty and 10 years manufacturing warranty. It should be provided On Stamp Paper by contractor/Company.
2 | Inverters (5KW) | 2 |  | 0
SMART Off-grid, with Grid sharing option
-Complete plug n play system
The Inverter should be Lithium Ion Compatible
- With all accessories including Inverter, Circuit Breakers and Change over switch etc. in one presentable cabinet
-Real time Grid Sharing
The inverter should be able to work without batteries too.
The inverter must be user programmable for selecting PV, Grid and Battery Priority as well as Built-in programmed
Inverter must be capable of configuring for charging Lithium Ion Batteries.
- Protection against over/under voltage, current and reverse polarity
Warranty: Min. 2 Years
3 | Dry Gel Batteries. | 12 |  | 0
12V 200 AH.
Warranty: 2 Years Minimum.
2000 cycle at 50% DOD at discharge a rate of 10 hours.
4 | PV Mounting Structure & base foundation Channel (for PV Modules) 14 Gauge with SS Nuts & Bolts & fixed to the roof of the building or ground with Anchor Bolts Fixed in proper location able to withstand highspeed winds | Set |  | 0
5 | Installation & Transportation per site (lumpsum for 1 site) | Lumpsum |  | 0
Installation should include all mandatory AC/DC Breakers, 1P & 2P where required.
DC Flexible Copper Cables 6mm2 single core per string fitted in HDPE Pipe (1”) & 35mm2 Single Core Cable between Inverter & Battery Bank. Inauguration/Sign Board, Earthing Road 5 Feet Long, 12mmDia & Earthing Powder, Switches 10/15 Amp. On/Off Switches, Plug & DB, Copper Thimbles, Sleeves Butt Joint connectors, ring thimbles, PVC Shrouds, Heat Shrink Tubes for all termination, connection & jointing as per International practice. Inverter Batters & Protective Devices must be labeled properly. Cabinet for Complete System. (Inverter, Batteries, Stabilizer etc) A complete dedicated indoor high-quality fitting with duct patti for all the equipment in use. Detail User Manual for end User having complaint number
| Sub-Total for per Site |  |  | 0
| Grand Total in PKR (3 Sites) |  |  | 0