{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Sheet1"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":17,"n_cols":4,"rows_kept":17,"cut":false,"hidden":false,"merged":[]}
[null,null," Rehabilitation of Azragiya Central Water Planet in Falluja"]
["Item # in BOQ","Item","Required Specifications","Submitted Specifications"]
[" Item 1","Horizontal split case pump of (540m3x75m) capacity"," Shaft: Stainless steel;\nOpen: 12\",with electrical starter;\n Impeller: bronze;\n Motor: IP55;\n Isolation class: f;\n Electrical engine: 200-250kW;\n  Voltage: 380 – 400 Va;\n Speed: 1500 RPM;\n Main frequency: 50hz;\nEnclosure class: 55;\nRated: v3 phase.\n Preferred brands are (Caprari, Flowserve, Cornell) or equivalent. Certificate of origin and BV inspection are required."]
[" Item 2","Horizontal split case pump of (720m3x20m) capacity"," Shaft: Stainless steel;\nOpen: 12\",with electrical starter;\n Impeller: bronze;\n Motor: IP55;\n Isolation class: f;\n Electrical engine: 200-250kW;\n  Voltage: 380 – 400 Va;\n Speed: 1500 RPM;\n Main frequency: 50hz;\nEnclosure class: 55;\nRated: v3 phase.\n Preferred brands are (Caprari, Flowserve, Cornell) or equivalent. Certificate of origin and BV inspection are required."]
[" Item 3","Horizontal split case pump for mud of (150m3x30m)capacity","Shaft: Stainless steel;\nOpen: 12\",with electrical starter;\nImpeller: bronze;\n Motor: IP55;\n Isolation class: f;\n Electrical engine: 37-50kW;\n  Voltage: 380 – 400 Va;\n Speed: 1500 RPM; \nMain frequency: 50hz;\n Enclosure class: 55;\n Rated: v3 phase;\n Brands are (Caprari, Flowserve, Cornell) or equivalent. Certificate of origin and BV inspection are required."]
[" Item 4"," Horizontal split case pump of (600m3x6m) capacity","Shaft: Stainless steel;\nOpen: 12\",with electrical starter;\nImpeller: bronze;\n Motor: IP55;\n Isolation class: f;\n Electrical engine: 37-50kW;\n  Voltage: 380 – 400 Va;\n Speed: 1500 RPM; \nMain frequency: 50hz;\n Enclosure class: 55;\n Rated: v3 phase;\n Brands are (Caprari, Flowserve, Cornell) or equivalent. Certificate of origin and BV inspection are required."]
[" Item 5","Kiosk distribution transformer rate 1600 Kva","See Annex A"]
[" Item 11","Electrical starter of two stages (Star-Delta) and 55kW capacity"," The metal box of (80*60*25)cm;\n The main circuit breaker is 200 ampere;\nConnectors 80-100 ampere;\n Phase filler;\n Electronic screen ;\n Sensors.\n Preferred brands for the parts are ABB, Schneider, Siemens or equivalent. "]
[" Item 14","PLC main cabinet","Boards;\n Two main circuit breakers of four phases and 2500 ampere capacity;\n Six sub circuit breakers of three phases and 630 ampere capacity;\n Four circuit breakers of three phases and 150 ampere capacity;\n Six circuit breakers of three phases and 100 ampere capacity;\n Twelve sub circuit breakers of 40-70 ampere capacities;\nPassbars;\nDigital screens;\n Cables.\n Preferred brands for the parts are ABB, Schneider, Siemens or equivalent. "]
[" Item 18"," Electrical bridge crane of 1 ton capacity","Four-side moves (two speeds for up, down, forward and backward);\n Transport system (channel and angle sections);\n Festoon cable with 9m depth;\n Electrical operations system;\n Over-load and bend sensors.\n Preffered brands are Hitachi, GIS, Yale, KM or equivalent."]
[" Item 19","Electrical bridge crane of 3 ton capacity","Four-side moves (two speeds for up, down, forward and backward);\n Transport system (channel and angle sections);\n Festoon cable with 9m depth;\n Electrical operations system;\n Over-load and bend sensors.\n Preffered brands are Hitachi, GIS, Yale, KM or equivalent."]
[" Item 20","Lectrical bridge crane of 5 ton capacity","Four-side moves (two speeds for up, down, right and left) ;\nAlongside the pump hall not less than 60m;  Transport system (channel and angle sections);\n Festoon cable with 12m depth;\n Electrical operations system;\n Over-load and bend sensors.\n Preffered brands are Hitachi, GIS, Yale, KM or equivalent."]
[" Item 25"," Generator of 500 kVA capacity","See Annex A"]
[" Item 26","Generator of 1500 kVA capacity ","See Annex A"]
[" Item 27","Chlorine sterilization device of 10 kg/hr capacity ","With 10 horses posters and cooper pipes;\n System of liquid chlorine blockage;\n Heater;\n Pressure regulator for the chlorine gas of (0-10) bar capacity;\nElectrical valve to stop the chlorine gas flow;\n Pressure gauge of 10 bar capacity;\nWater injector;\nFilter at the entrance of the device. "]
[" Item 28"," Alum injection device of 750 ltr/hr capacity","Alum mixer of 4 horses capacity;\n Shaft: stainless steel ;\n PPR pipes."]
[" Item 29","Electrical gate valves","Double flanges and 300mm size;\n Designed for the high pressures;\n Operated by electrical engine (ON/OFF). Preffered brands are VAG, DOGUS, UBNT or equivalent."]