{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Sheet1"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":13,"n_cols":4,"rows_kept":13,"cut":false,"hidden":false,"merged":[]}
[null," Rehabilitation of Albu-Jabur, Albu-Khalifa and Albu-Ghanim Water Complexes"]
["Item # in BOQ","Item","Required Specifications","Submitted Specifications"]
["Part 1: Item 1","pump of (200 m3/hr*60m) capacity"," Pump Type:Horizontal Split Case Water Pump,Heavy duty application, soft backing, mechanical lubrication unit;\nShaft:Stainless steel - GG25 (AISI420);\nImpeller: bronze;\nsuction hole:PN 150 DN16\nDelivery hole:PN125DN16\nMotor:IP55, Isolation class = f;\nVoltage:380 – 400 Va;\nSpeed:1500 RPM;\nMain frequency:50hz;\nEnclosure class:55;\nRated:v3 phase;\nWith electrical Starter\nPreferred brands are GRUNDFOS, KSB, PENTAX, Wilo or equivalent. Origin certificate and test certificate BV are required\n\n"]
["Part 1: Item 2","Supply and install submersible pump of (200 m3/hr*20m) capacity","Power:22.5\nShaft:Stainless steel - GG25 (AISI420);\nRotation:1500 RBM\nImpeller: bronze;\nVoltage:380 – 400 Va;\nRated:v3 phase;\nMotor:IP55, Isolation class = f;\nSuction hole :8 inch;\nDelivery hole:6 inch;\nProtected against water leakage\nStar- delta electrical motor with its starter.\nPreferred brands are GRUNDFOS, KSB, PENTAX, Wilo or equivalent. Origin certificate and test certificate BV are required\n\n"]
["Part 1: Item 8","electrical generator of 250kVa ","See Annex (A)"]
["Part 2: Item 1","pump of (200 m3/hr*60m) capacity"," Pump Type:Horizontal Split Case Water Pump,Heavy duty application, soft backing, mechanical lubrication unit;\nShaft:Stainless steel - GG25 (AISI420);\nImpeller: bronze;\nsuction hole:PN 150 DN16\nDelivery hole:PN125DN16\nMotor:IP55, Isolation class = f;\nVoltage:380 – 400 Va;\nSpeed:1500 RPM;\nMain frequency:50hz;\nEnclosure class:55;\nRated:v3 phase;\nWith electrical Starter\nPreferred brands are GRUNDFOS, KSB, PENTAX, Wilo or equivalent. Origin certificate and test certificate BV are required\n\n"]
["Part 2: Item 2","Supply and install submersible pump of (200 m3/hr*20m) capacity","Power:22.5\nShaft:Stainless steel - GG25 (AISI420);\nRotation:1500 RBM\nImpeller: bronze;\nVoltage:380 – 400 Va;\nRated:v3 phase;\nMotor:IP55, Isolation class = f;\nSuction hole :8 inch;\nDelivery hole:6 inch;\nProtected against water leakage\nStar- delta electrical motor with its starter.\nPreferred brands are GRUNDFOS, KSB, PENTAX, Wilo or equivalent. Origin certificate and test certificate BV are required\n\n"]
["Part2: Item 7","electrical generator of 250kVa ","See Annex (A)"]
["Part 2: Item 8","transformer 250 kVa capacity"," Name of manufacturer: ABB , Schneider Siemens or equivalent ;\nRated Voltage :11-0.416 kV ;\nRated KVA :250KVA ;\nRated power factor :0.8;\nNo. of Phase: 3Ph  ;\nHighest system voltage:12000 volts;\nSystem:3- phase,3-wire with neutral isolated but provision is made for earthling through an earthling resistance of 21.1 ohms to limit, The earth fault current to 300 Amp;\nNominal voltage system : 416/240 volts s;\nShort circuit level: According to the short circuit level of H.T side and the rated power of the transformer;\nShort circuit level: 25 KA at 11000 volts;\nFrequency:50Hz  ;\nInterphase Connection:  H.V. Delta L.V- star with neutral brought out;\nVector relationship : Dyn 11;\nType of Cooling: ONAN ;\nType :Outdoor type ;\nTapings change:  five tapping for – 2.5% - 5% on the H.T winding for off Circuit operation externally. The machine must be of the robust and definite position type with a click indicating position arrived during tap changing.\n\n"]
["Part 3: Item 1","pump of (200 m3/hr*60m) capacity"," Pump Type:Horizontal Split Case Water Pump,Heavy duty application, soft backing, mechanical lubrication unit;\nShaft:Stainless steel - GG25 (AISI420);\nImpeller: bronze;\nsuction hole:PN 150 DN16\nDelivery hole:PN125DN16\nMotor:IP55, Isolation class = f;\nVoltage:380 – 400 Va;\nSpeed:1500 RPM;\nMain frequency:50hz;\nEnclosure class:55;\nRated:v3 phase;\nWith electrical Starter\nPreferred brands are GRUNDFOS, KSB, PENTAX, Wilo or equivalent. Origin certificate and test certificate BV are required\n\n"]
["Part 3: Item 2","Supply and install submersible pump of (200 m3/hr*20m) capacity","Power:22.5\nShaft:Stainless steel - GG25 (AISI420);\nRotation:1500 RBM\nImpeller: bronze;\nVoltage:380 – 400 Va;\nRated:v3 phase;\nMotor:IP55, Isolation class = f;\nSuction hole :8 inch;\nDelivery hole:6 inch;\nProtected against water leakage\nStar- delta electrical motor with its starter.\nPreferred brands are GRUNDFOS, KSB, PENTAX, Wilo or equivalent. Origin certificate and test certificate BV are required\n\n"]
["Part3: Item 7","electrical generator of 250kVa ","See Annex (A)"]
["Part3: Item 8","transformer 250 kVa capacity"," Name of manufacturer: ABB , Schneider Siemens or equivalent ;\nRated Voltage :11-0.416 kV ;\nRated KVA :250KVA ;\nRated power factor :0.8;\nNo. of Phase: 3Ph  ;\nHighest system voltage:12000 volts;\nSystem:3- phase,3-wire with neutral isolated but provision is made for earthling through an earthling resistance of 21.1 ohms to limit, The earth fault current to 300 Amp;\nNominal voltage system : 416/240 volts s;\nShort circuit level: According to the short circuit level of H.T side and the rated power of the transformer;\nShort circuit level: 25 KA at 11000 volts;\nFrequency:50Hz  ;\nInterphase Connection:  H.V. Delta L.V- star with neutral brought out;\nVector relationship : Dyn 11;\nType of Cooling: ONAN ;\nType :Outdoor type ;\nTapings change:  five tapping for – 2.5% - 5% on the H.T winding for off Circuit operation externally. The machine must be of the robust and definite position type with a click indicating position arrived during tap changing.\n\n"]