{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Sheet1"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":16,"n_cols":4,"rows_kept":16,"cut":false,"hidden":false,"merged":[]}
[null,null,"  Rehabilitation of  E3& M2 Lift Stations"]
[null,null,"Ramadi - Anbar"]
["Item # in BOQ","Item","Required Specifications","Submitted Specifications"]
["Part 1: Item 1","Submersible pump of Q(max)=1000m3/hr and H(max)=29m capacity","R.P.M=1500 Sires;\nSuction 10 inch;\nSolid passage 150mm at least;\nShaft is stainless steel;\nImpeller of good cast iron;\nIP=68, wight 1000 kg at least;\nSignal channel;\nWear ring from steel/rubber;\nMechanical seal from silicon carbide/ceramic for pump.\nPreferred brands are Wilo, Cap, Caprari, Flyget, Cornell or equivalent.\nCertificate of origin and BV inspection are required."]
["Part 1: Item 2","Electrical (Soft Starter) to (ON/OFF) for the pumps","55 kW capacity ;\n With metal board ;\n Maincircuit breaker of 250 amp.\nPreferred brands are ABB, Schneider, Siemens or equivalent."]
["Part 1: Item 3"," Pump horizontal for sewage of Q=600m3/hr and Head 21m","Consist of End suction pump, motor, Coupling, baseplate;\n Steel Bar Pump ; \n Efficiency 66.4% at  least ;\nShaft From AISI 420;\n10\" suction;\nImpeller (ø330 mm) open two vane (blades) Stainless steel (AISI);\n Solid Size 105 ø ;\nMotor 75KW at least ;\n IE2, IP55, insulation Class F ;\n1500 RPM series.\nPreferred brands are (Flygit, ,Cornell , Calalla ,Flow-Serve, ,Grandfos) .Certificate of origin and BV inspection are required.  "]
["Part 1: Item 4","Main distribution board","Metal board box Mikano;\n Main circuit breaker (4 poles )(630A); \n 3 circuit breakers (3 poles) (250A);\n12 contactors of 120A  ;\n 4 digits screen;\n Phase filers;\n Timer (work by floating automatic ).  Preferred brands are ABB, Schneider, Siemens or equivalent."]
["Part 1: Item 5"," Electrical change over system","1200 amp capacity ; \n With metal board of 70*60*30cm size ; passbars;\n multi digit screen (V, A, Hz).\n Preferred brands are ABB, Schneider, Siemens or equivalent."]
["Part 1: Item 11","Mobile diesel-powered pump"," Motor pump type LR 25/FL;\n Flow (Qmax) : 60 m3/hr;\nHead(Hmax) =118m;\n Type: Multistage 2 impeller;\n Engine: 25.5hp Air cooling;\n  hose of 4 inch size and 350m length; With plugged, clamps."]
["Part 1: Item 13"," generator of 250 Kva","See Annex A"]
["Part 2: Item 1"," submersible pump Q(max)=400m3/hr andH(max)=33m"," R.P.M=1500 Sires;\n Suction 6 inch;\n Solid passage 150mm at least;\n Shaft is stainless steel;\nImpeller of good cast iron;\n IP=68, wight 380 kg at least;\n Singal channel;\n Wear ring from steel/rubber;\n Mechanical seal from silicon Carbide/caribide for pump.\n Preferred brands are Wilo, Cap, Caprari, Flyget, Cornell or equivalent. \nCertificate of origin and BV inspection are required."]
["Part 2: Item 3","Main distribution board","With Metal board box Mikano;\n Main circuit breaker (4 poles )(400A); \n 3 circuit breakers (3 poles) (160A);\n 6 contactors of 60A  ;\n 4 digits screen;\n Phase filers;\n Timer (work by floating automatic ).  Preferred brands are ABB, Schneider, Siemens or equivalent."]
["Part 2: Item 4"," Electrical change over system","630 amp capacity ; \nWith the metal board of 40×60*30cm size ; Passbars;\n Multi digit screen (V, A, Hz).\n Preferred brands are ABB, Schneider, Siemens or equivalent."]
["Part 2: Item 8","Mobile diesel-powered pump"," Motor pump type LR 25/FL;\n Flow (Qmax) : 60 m3/hr;\nHead(Hmax) =118m;\n Type: Multistage 2 impeller;\n Engine: 25.5hp Air cooling;\n Hose of 4 inch size and 350m length; With plugged, clamps."]
["Part 2: Item 10"," generator of 250 Kva","See Annex A"]
["Part 2: Item 11"," electrical crane","  Two speed with the pulley ;\nIron chain,wagon;\n Capacity : 3 Ton ;\n Power : 1.45 /0.36 kw ;\nDepth : 6m at least .\nPreferred brands are GIS or KM"]