{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Sheet1"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":9,"n_cols":4,"rows_kept":9,"cut":false,"hidden":false,"merged":[[8,0,9,0],[8,1,9,1],[8,2,9,2],[8,3,9,3]]}
[null,null,"  Rehabilitation of Al-Sikak Water Complex "]
["Item # in BOQ","Item","Required Specifications","Submitted Specifications"]
["Item 1","electrical generator of 250kVa ","See Annex (A)"]
["Item 5"," horizontal pump of (200 m3/hr*60m) capacity","\nShaft:Stainless steel - GG25 (AISI420);\nImpeller: oil bronze;\nsuction hole:PN 150 DN16\nDelivery hole:PN125DN16\nPower of electrical motor:55 KW;\nMotor:  IP:55, Isolation class = f;\nVoltage:380 – 400 Va;\nSpeed:1500 RPM;\nMain frequency:50hz;\nCupper Coil;\nRated:v3 phase;\nWith electrical Starter.\n Origin certificate and test certificate BV are required"]
["Item 6"," horizontal pump of (100 m3/hr*60m) capacity","\nShaft:Stainless steel - GG25 (AISI420);\nImpeller: oil bronze;\nsuction hole:PN 150 DN16\nDelivery hole:PN125DN16\nPower of electrical motor : 30 KW;\nMotor:  IP:55, Isolation class = f;\nVoltage:380 – 400 Va;\nSpeed:1500 RPM;\nMain frequency:50hz;\nCupper Coil;\nRated:v3 phase;\nWith electrical Starter.\n Origin certificate and test certificate BV are required"]
["Item 11","submersible pump of (50 m3/hr*30m) capacity","\nShaft  :Stainless steel - GG25 (AISI420);\nRotation:1500 RBM\nImpeller: Stainless steel;\nVoltage:380 – 400 Va;\nPower: 18 KW\nRated: v3 phase;\nMotor:IP 68, Isolation class = f;\nProtected against water leakage\nStar- delta electrical motor with its starter;\nCupper Coil.\nOrigin certificate and test certificate BV are required\n"]
["Item 13"," horizontal pump of (100 m3/hr*20m) capacity","\nShaft:Stainless steel - GG25 (AISI420);\nImpeller: oil bronze;\nsuction hole:PN 150 DN16\nDelivery hole:PN125DN16\nPower of electrical motor : 30 KW;\nMotor:  IP:55, Isolation class = f;\nVoltage:380 – 400 Va;\nSpeed:1500 RPM;\nMain frequency:50hz;\nCupper Coil;\nRated:v3 phase;\nWith electrical Starter.\n Origin certificate and test certificate BV are required"]
["Item 18","electrical generator of 30 kVa ","See Annex (B)"]
["Item 23"," transformer 630 kVa "," Rated Voltage :11-0.416 kV\nRated KVA : 630 kVA \nRated power factor :0.8\nNo. of Phase: 3Ph  \nHighest system voltage:12,000 volts\nSystem: 3- phase, 3-wire with neutral isolated but provision is made for earthling through an earthling resistance of 1.1 ohms to limit, The earth fault current to 300 Amp.\nLow voltage side:\nNominal voltage system : 416/240 volts s\nShort circuit level: According to the short circuit level of H.T side and the rated power of the transformer\nShort circuit level: 25 KA at 11000 volts\nFrequency: 50Hz  \nInterphase Connection:  H.V. Delta L.V- star with neutral brought out.\nVector relationship : Dyn 11\nType of Cooling: ONAN \nType :Outdoor type \nTapings change:  five tapping for – 2.5% - 5% on the H.T winding for off Circuit operation externally. The machine must be of the robust and definite position type with a click indicating position arrived during tap changing.\n11 kV side terminal: clamp type with eyebolt and nut suitable for conductors up to 150 mm2 copper.\nlow voltage terminal:  flat bar type with holes suitable for 7x1x150 mm2 copper\nGeneral:\nAmbient temperature :\n                                       Maximum:55/C\n                                       Minimum:-10/C   \nRelative Humidity : around 60% at maximum temperature \nAltitude : (1000m) From sea level\nNo of phases: 3PH \nFrequency: 50Hz  \nSystem Voltage  :11, 0.4 KV \nMake: Original manufacturer (Local Assembled Not acceptable)\nRequired documents: manufacturer certification, single line diagram and detailed drawing brochure catalogue are required."]