{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Hay-Al Askary Network & Feeder "],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":2,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Hay-Al Askary Network & Feeder ","index":0,"n_rows":49,"n_cols":6,"rows_kept":49,"cut":false,"hidden":false,"merged":[[8,5,9,5],[8,4,9,4],[8,3,9,3],[8,2,9,2],[8,0,9,0],[1,2,1,5],[6,5,7,5],[6,4,7,4],[6,3,7,3],[6,2,7,2],[33,0,33,5],[34,2,34,5],[12,2,13,2],[16,0,17,0],[14,5,15,5],[14,4,15,4],[14,3,15,3],[14,2,15,2],[14,0,15,0],[16,5,17,5],[16,4,17,4],[16,3,17,3],[16,2,17,2],[22,3,23,3],[22,4,23,4],[22,5,23,5],[18,5,19,5],[18,4,19,4],[18,3,19,3],[18,2,19,2],[32,1,32,2],[0,1,0,5],[28,0,29,0],[28,2,29,2],[28,3,29,3],[28,4,29,4],[28,5,29,5],[24,0,25,0],[24,2,25,2],[24,3,25,3],[24,4,25,4],[24,5,25,5],[4,0,5,0],[4,2,5,2],[4,3,5,3],[4,4,5,4],[4,5,5,5],[10,5,11,5],[10,4,11,4],[10,3,11,3],[10,2,11,2],[10,0,11,0],[12,5,13,5],[12,3,13,3],[6,0,7,0],[35,2,35,5],[35,0,35,1],[34,0,34,1],[1,0,1,1],[2,0,2,5],[30,0,31,0],[26,5,27,5],[26,4,27,4],[26,3,27,3],[26,2,27,2],[26,0,27,0],[30,5,31,5],[30,4,31,4],[30,3,31,3],[30,2,31,2],[22,0,23,0],[12,0,13,0],[18,0,19,0],[20,5,21,5],[20,4,21,4],[20,3,21,3],[20,2,21,2],[20,0,21,0],[22,2,23,2],[36,0,36,5],[38,0,39,0],[38,2,39,2],[38,3,39,3],[38,4,39,4],[38,5,39,5],[40,0,41,0],[40,2,41,2],[40,3,41,3],[40,4,41,4],[40,5,41,5],[52,0,52,5],[45,1,45,4],[42,0,43,0],[42,2,43,2],[42,3,43,3],[42,4,43,4],[42,5,43,5],[48,0,48,5],[50,0,50,4],[49,0,49,4],[51,0,51,4],[47,0,47,4],[44,1,44,2]]}
[null,"Bill of Quantities/ Lot1"]
["ITB 187/16 - Rehabilitation of the Electrical Network in Hay Al-Askary Quarter, Al-Udhaim Sub-district, Diyala Governorate                                          ",null,"تأهيل شبكة كهرباء الحي العسكري في ناحية العظيم , ديالى "]
["All equipment and materials must be new and compatible with Iraqi Specifications and attached annexes\nجميع المعدات والمواد يجب ان تكون جديدة ومطابقة لمواصفات وزارة الكهرباء العراقية والملاحق المرفقة"]
["#","Items /Descriptions/ specifications of materials ","Unit","Quantity","Price in USD","Total in USD"]
[1,"Supply, Install, test and commission of outdoor type distribution transformer 11/0.4KV capacity  400kVA with   two galvanized Electrical poles 11m  ST 52, concreting foundation diminutions (40cm ,40cm ,120cm) with concrete design mixing  4:2:1 cover all concert foundation with Asphalt Paint (flunkout), earthing system for both Neutral point and frame of the transformer using  copper cable 1cx50mm2 with 10m length and two earth rods (1.5m)  to be connecting from  both sides of transformer with  all necessary accessories clamps, glands  ,nuts and bolts, connect set link fuses with lighting arrester and all suspending necessary accessories , supply  and connect with each transformer Electrical Metal  panel Board  consist with  two   MCCB  400A with all connection accessories  ,board connect  with low side of transformer throw copper cables 1cx150mm2  with length 80 m  from both  side  with all necessary accessories need glands, clamps,  and connect with overhead line through Aluminum –Copper clamps, the support for transformer  set galvanizes bracket( 210cm ) L Channel type  with 80cm U Channel type  with all necessary accessories of installation and connecting for  H.T  side of transformer with link fuse using ACC wire 50mm2 and connect Cutout Fuse with 120/20 for overhead lines using Aluminum –Aluminum clamps .all the electrical   works will be completed under instruction and supervision of the committee.             See Annex (1) for distribution transformer                                                    Annex (4) for transformer distribution boards                                            Annex (7)- Expulsion Fuse- Cutouts- 11KV","Ea.",5,null,{"$f":"E5*D5","v":0}]
[null,"تجهيزونصب وفحص وتشغيل محولة توزيع كهرباء خارجية 04/11 ذات سعة 400 كي في اي كاملة. نصبهاعلى 2 عمود مدورة ض.ع مغلون 11متر st-52وصب القواعد  كونكريتية لهما بنسبة خلط 1:2:4باستخدام السمنت المقاوم للاملاح بابعاد (40سم 40Xسم 210Xسم) وطلاء القاعدة  الكونكريتية للعمود بالزفت (فلينكوت )مع تاْ ريض جهتي المحولة المحايد والبدن باستخدام سلك نحاس 50ملم 2 بطول 10م وقابلو نحاس (1*50ملم ) طول 10م مع قضيبي تأريض /2 يطول 1.5م مع كافة ادوات الربط من القفيص والبراغي والجنلات مع ربط سيت من كت اوف فيوز مع مانعة الصواعق وكل ملحقات الربط وتجهيز كل محولة ببورد كهرباء حديدي مصبوغ  المتكون من صندوق حديدي  بداخلها قواطع دورة عدد/2 400امبر مع كل الملحقات النظامية للبورد المحولة .تربط عليها كيبلات الخطوط 1*150ملم 2نحاس بطول 80متر لجهتي المحولة مع كل ملحقات الربط وتثبط المحولة على قاعدة براكيت جنل 210سم مغلون واستخدام جنل ساقية 3انج 80سم  وربط جهة الضغط العالي للمحولة مع منظومة كت او بواسطة سلك المنيوم 50ملم وربط كت اوف مع اسلاك ض.ع120/20ملم تم اكمال العمل بموجب المواصفات وتوجيهات اللجنة المشرفة"]
[2,"Supply Install test and commission of outdoor type distribution transformer 11/0.4KV capacity  250kVA  with two galvanized Electrical poles 11m  Height  ST 52 type, the foundation for transformer base concrete with diminutions (40cm ,40cm ,120cm) with concrete  design mixing 4:2:1 cover all concert foundation with Asphalt Paint (flunkout) earthing system for both Neutral point and the  frame of transformer using  copper cable 1cx 50mm2 with10m length,  and two earth rods (1.5m) earth to be  connecting from  both sides of transformer with all necessary accessories clamps, glands  ,nuts and bolts. connect set link fuses with lighting arrester and all suspending accessories, supply and connect with each transformer Electrical Metal  panel Board  consist with two MCCB  250A with all connection accessories  ,board connect  with low side of transformer throw copper  cables 1cx 150mm2. other side connect with overhead line through Aluminum –Copper clamps,  the support for transformer  set galvanizes bracket( 210cm ) L Channel type  with 80cm U channel type with all accessories of installation, connecting H.T  side of transformer with link fuss using ACC wire 50mm2 , and connect Cutout fuse side with 120/20 overhead lines using Aluminum –Aluminum clamps ..all the electrical   works will be completed under instruction and supervision of the committee.                                             See Annex (1) for distribution transformer                                                                    Annex (4) for transformer distribution boards                                                  Annex (7)- Expulsion Fuse- Cutouts- 11KV","Ea.",5,null,{"$f":"E7*D7","v":0}]
[null,"تجهيزونصب وفحص وتشغيل محولة توزيع كهرباء خارجية 04/11 ذات سعة 250 كي في اي كاملة. نصبهاعلى 2 عمود مدورة ض.ع مغلون 11متر st-52وصب القواعد  كونكريتية لهما بنسبة خلط 1:2:4باستخدام السمنت المقاوم للاملاح بابعاد (40سم 40Xسم 210Xسم) وطلاء القاعدة  الكونكريتية للعمود بالزفت (فلينكوت )مع تاْ ريض جهتي المحولة المحايد والبدن باستخدام سلك نحاس 50ملم 2 بطول 10م وقابلو نحاس (1*50ملم ) طول 10م مع قضيبي تأريض /2 يطول 1.5م مع كافة ادوات الربط من القفيص والبراغي والجنلات مع ربط سيت من كت اوف فيوز مع مانعة الصواعق وكل ملحقات الربط وتجهيز كل محولة ببورد كهرباء حديدي مصبوغ  المتكون من صندوق حديدي  بداخلها قواطع دورة عدد/2 250امبر مع كل الملحقات النظامية للبورد المحولة .تربط عليها كيبلات الخطوط 1*150ملم 2نحاس بطول 80متر لجهتي المحولة مع كل ملحقات الربط وتثبط المحولة على قاعدة براكيت جنل 210سم مغلون واستخدام جنل ساقية 3انج 80سم  وربط جهة الضغط العالي للمحولة مع منظومة كت او بواسطة سلك المنيوم 50ملم وربط كت اوف مع اسلاك ض.ع120/20ملم تم اكمال العمل بموجب المواصفات وتوجيهات اللجنة المشرفة"]
[3,"Supply Install test H.T  galvanized Electrical tubular poles 11m Height              ST 52 type, the work including excavation for  pole foundation (50cm *50cm*180cm ) concreting foundation diminutions  formwork concert (40cm ,40cm ,210cm) with concrete design mixing  4:2:1 cover all concert foundation with Asphalt Paint (flunkout), connect earthing  using  copper cable               1cx 50mm2 the pole be connected  with earth rods  ( 1.5m) length   with all necessary  accessories Copper  clamps, glands, nuts and bolts , and to be backfill space between bole foundation and excavated area with a suitable backfill soil with very good compaction ,  and making the alignment for the pole, and the connection with all necessary  accessories, clamps, glands  ,nuts  bolts and washer .    all the electrical   works will be completed under instruction and supervision of the committee.                                                                   See Annex (9) for tubular poles 11m  ST- 52                                                   ","Ea.",15,null,0]
[null,"تجهيزونصب وفحص عمود مدورة ض.ع مغلون 11متر st-52و يشمل العمل حفر قاعدة  العمود بابعاد ( 40سم *40سم *180سم )وصب قاعدة بنسبة خلط 1:2:4باستخدام السمنت المقاوم للاملاح بابعاد (40سم 40Xسم 210Xسم) وطلاء القاعدة  الكونكريتية للعمود بالزفت (فلينكوت )ويتم مليء الفراغ بين الحفر وقاعدة العمود بمواد دفن مناسبة يقبل الحدل لدرجة تمنع ميلان العمود ثم  تاْ ريض  العمود باستخدام سلك نحاس 50ملم 2 بطول1.5م مع قضيب ارضي 1.5م  مع كافة ادوات الربط من القفيص والبراغي يتم اكمال العمل بموجب المواصفات وتوجيهات اللجنة المشرفة"]
[4,"Supply, Install and test H.T galvanized Electrical lattice poles 11m Height  ST- 52 type  work including excavation pole foundation (50cm *50cm*180cm ) concreting foundation diminutions  formwork concert (40cm ,40cm ,210cm) with concrete design mixing  4:2:1 cover all concert foundation with Asphalt Paint (flunkout) connect earthing  using  copper cable 1cx 50mm2 with  1.5m length   the pole be connected  with earth rods (1,5m) with all accessories Copper  clamps, glands, nuts and bolt, backfill space between bole foundation and excavated area with a suitable backfill soil with very good compaction and making the alignment for the pole, and the connection with all necessary  accessories, clamps, glands  ,nuts  bolts and washer .   all the electrical   works will be completed under instruction and supervision of the   committee.                                      See Annex (6) for Lattice poles 11m  ST- 52","Ea.",39,null,0]
[null,"تجهيزونصب وفحص عمود مشبك  ض.ع مغلون 11متر  ST-52و يشمل العمل حفر قاعدة  العمود بابعاد ( 50سم *50سم *180سم )وصب قاعدة بنسبة خلط 1:2:4باستخدام السمنت المقاوم للاملاح بابعاد (40سم 40Xسم 210Xسم) وطلاء القاعدة  الكونكريتية للعمود بالزفت (فلينكوت )ويتم مليء الفراغ بين الحفر وقاعدة العمود بمواد دفن مناسبة يقبل الحدل لدرجة تمنع ميلان العمود ثم  تاْ ريض  العمود باستخدام سلك نحاس 50ملم 2 بطول1.5م مع قضيب ارضي 1.5م  مع كافة ادوات الربط من القفيص والبراغي يتم اكمال العمل بموجب المواصفات وتوجيهات اللجنة المشرفة"]
[5,"Supply ,Install and test L.T  galvanized Electrical tubular poles 9 m Height  ST 52 type  work including excavation pole foundation (50cm *50cm*150cm ) concreting foundation diminutions  formwork concert (40cm ,40cm ,180cm) with concrete  design mixing  4:2:1 cover all concert foundation with Asphalt Paint (flunkout) connect earthing  using  copper cable 1cx 50mm2  with 1.5m length  to be  connected  with earth rods (1,5m) with all accessories Copper  clamps, glands, nuts and bolt , backfill space between bole foundation and excavated area with a suitable backfill soil with very good compaction , and making the alignment for the pole . All the electrical   works should be completed under the instruction and supervision of the committee                                                                                  See Attached Annex (9) for Tubular  poles 9m  ST- 52  ","Ea.",93,null,{"$f":"E13*D13","v":0}]
[null,"تجهيزونصب وفحص عمود مدورة ض .و مغلون 9متر st-52و يشمل العمل حفر قاعدة  العمود بابعاد ( 50سم *50سم *150سم )وصب قاعدة بنسبة خلط 1:2:4باستخدام السمنت المقاوم للاملاح بابعاد (40سم 40Xسم 180Xسم) وطلاء القاعدة  الكونكريتية للعمود بالزفت (فلينكوت )ويتم مليء الفراغ بين الحفر وقاعدة العمود بمواد دفن مناسبة يقبل الحدل لدرجة تمنع ميلان العمود ثم  تاْ ريض  العمود باستخدام سلك نحاس 50ملم 2 بطول1.5م مع قضيب ارضي 1.5م  مع كافة ادوات الربط من القفيص والبراغي يتم اكمال العمل بموجب المواصفات وتوجيهات اللجنة المشرفة"]
[6,"Supply ,Install, and  test L.T  galvanized Electrical Lattice  9 m Height  ST 52  type work including excavation pole foundation (50cm *50cm*150cm ) concreting foundation diminutions  formwork concert (40cm ,40cm ,180cm) with concrete design mixing  4:2:1 cover all concert foundation with Asphalt Paint (flunkout) connect earthing  using  copper cable 1cx 50mm2 with 1.5m length to be connected  with earth rods (1,5m) with all accessories Copper  clamps, glands, nuts and bolt , backfill space between bole foundation and excavated area with a suitable backfill soil with very good compaction , and making the alignment for the pole . all the electrical   works will be completed under instruction and supervision of the   committee                                                                                 See Annex (6) for Lattice  poles 9m  ST- 52","Ea.",78,null,0]
[null,"تجهيزونصب وفحص عمود مشبك  ض .و مغلون 9متر st-52و يشمل العمل حفر قاعدة  العمود بابعاد ( 50سم *50سم *150سم )وصب قاعدة بنسبة خلط 1:2:4باستخدام السمنت المقاوم للاملاح بابعاد (40سم 40Xسم 180Xسم) وطلاء القاعدة  الكونكريتية للعمود بالزفت (فلينكوت )ويتم مليء الفراغ بين الحفر وقاعدة العمود بمواد دفن مناسبة يقبل الحدل لدرجة تمنع ميلان العمود ثم  تاْ ريض  العمود باستخدام سلك نحاس 50ملم 2 بطول1.5م مع قضيب ارضي 1.5م  مع كافة ادوات الربط من القفيص والبراغي يتم اكمال العمل بموجب المواصفات وتوجيهات اللجنة المشرفة"]
[7,"Supply, install and test 120cm galvanized Channel bracket with clamps, glands, nuts and bolt , and all necessary accessories and connection ,work will be   According to instruction  and supervision by the committee .","Ea.",133,null,{"$f":"E17*D17","v":0}]
[null,"تجهيز وربط وفحص براكيت جنل 120سم مع القفيص والبراغي يربط في اعلى العمود ض.ع وحسب توجيهات اللجنة المشرفة ."]
[8,"Supply, install and test Pin Insulator 11KV with Spindle  ,  and all necessary  connection and accessories needed , work will be  instruction  and supervision by the committee      See attached Annex  (5)for 11KV insulators .","Ea.",242,null,{"$f":"E19*D19","v":0}]
[null,"تجهيز وربط وفحص عازل 11 كي في مع الأسبندل وكافة الملحقات والتوصيلات المطلوبة وحسب توجيهات اللجنة المشرفة "]
[9,"Supply, install and test Disc Insulator 11KV with complete accessories , According to specifications,  with instruction and supervision by the committee. See attached Annex (5)for 11KV insulators .","Ea.",48,null,{"$f":"E21*D21","v":0}]
[null,"تجهيز  وفحص وربط اقراص توتير مزدوجة مع الملحقات  بموجب المواصفات وتوجيهات اللجنة المشرفة  ,"]
[10,"Supply, test and installation ACSR Wire (Aluminium) 120/20mm2  and according specifications , with instruction and supervision by the committee. See attached  Annex (2)for 11KV Aluminum Wire  .","m.l.",3600,null,{"$f":"E23*D23","v":0}]
[null,"تجهيز  وفحص وربط سلك المنيوم مسلح  120/20ملم2   بموجب المواصفات وتوجيهات اللجنة المشرفة "]
["11-","Supply, test , connect Aluminum -Aluminium clamps according specifications with instruction and supervision by the committee","Ea.",50,null,{"$f":"E25*D25","v":0}]
[null,"تجهيز وفحص قفيص ربط المنيوم المنيوم بموجب المواصفات وتوجيهات اللجنة المشرفة "]
["12-","Supply ,test and install AAC Wire (Aluminium) 95mm2  and  according attached specifications, with  instruction and  supervision by the Committee,  See attached Annexes(2)for 11KV Aluminum wire  .","Ea.",15000,null,{"$f":"E27*D27","v":0}]
[null,"تجهيز  وفحص وربط  سلك المنيوم مسلح  95ملم2   بموجب المواصفات وتوجيهات اللجنة المشرفة  ,"]
[13,"Supply ,test and install AAC Wire (Aluminium) 50 mm2   according specifications  with  instruction and   supervision by the committee      See attached  Annexes(2)for 11KV Aluminum wire  .","m.l.",5000,null,{"$f":"E29*D29","v":0}]
[null,"تجهيز  وفحص وربط وسحب وربط سلك المنيوم مسلح 50ملم2   بموجب المواصفات وتوجيهات اللجنة المشرفة  ,"]
["15-","Supply, connect and test LV Insulator installation with all connection and  necessary accessories needed. See attached Annex (5)for 11KV insulators .","Ea.",1250,null,{"$f":"E31*D31","v":0}]
[null,"تجهيز  وفحص وربط عازل مع القفيص والبراغي وحسب توجيهات اللجنة المشرفة "]
[null,"Sub total for Rehabilitation of Al-Udhaim Electrical Network USD:",null,null,null,{"$f":"SUM(F5:F31)","v":0}]
[]
["Bill of Quantities/ Lot 2 "]
["Upgrade the Transmission  Feeder line 33 KV, Al-Udhem Sub-district, Diyala Governorate                                                    ",null,"تأهيل خط مغذي 33كي في  / العظيم    "]
["All equipment and materials must be new and compatible with Iraqi Specifications and attached annexes\nجميع المعدات والمواد يجب ان تكون جديدة ومطابقة لمواصفات وزارة الكهرباء العراقية والملاحق المرفقة"]
["#","Items /Descriptions/ specifications of materials ","Unit","Quantity","Price in USD","Total in USD"]
[1,"Supply, test and installation ACSR Wire (Aluminium) 120/20mm2  and according specifications and to be  instruction  and supervision by the committee.  See attached Annex (2) for Aluminium wires ","m.l.",15000,null,{"$f":"E39*D39","v":0}]
[null,"تجهيز  وفحص وربط وفحص وربط سلك المنيموم مسلح  120/20ملم2   بموجب المواصفات وتوجيهات اللجنة المشرفة  ,"]
[2,"Supply install and test Pin Insulator 11KV with Spindle  according  and  to be   instruction  and supervision by the committee .                 See Annex (3) for insulation ","Ea.",1500,null,0]
[null,"تجهيز و فحص وربط عازل 33ك.ف مع سبندل بموجب المواصفات وتوجيهات اللجنة المشرفة  ,"]
[3,"Supply, test and install Disc Insulator 11KV with complete accessories  According to specifications and to be instruction and supervision by the committee   See Annex (3) for insulation ","Ea.",1500,null,0]
[null,"تجهيز  وفحص وربط اقراص توتير مزدوجة مع الملحقات  بموجب المواصفات وتوجيهات اللجنة المشرفة  ,"]
[null,"Sub total cost Upgrade the Transmission line Feeder 33 KV in USD:",null,null,null,{"$f":"SUM(F39:F43)","v":0}]
[null,"Total offered price in USD",null,null,null,{"$f":"SUM(F45,F33)","v":0}]
[]
["Name of the Company "]
["Signature/ Stamp  "]